## Slide 1: ZTF: Electronics Cooling
Michael Feeney
07.24.2017

## Slide 2: Introduction
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Series-Parallel
Rough Circuit Analysis
  Series-Parallel Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 3: Hardware Overview
Telescope Layout
  5X Archon Controllers (CCD controllers)
    Located at the base of the Camera Support Structure to minimize analog signal path length.
  Electronics Rack
    Located at the base of the telescope (reduces torque moment arm and is convenient for access).
Why cool?
  To assure that the electronics are operating at safe temperature ranges.
  To avoid putting warm air near the beam (convection cells) and compromising dome seeing.
Archons
Electronics Rack

## Slide 4: Hardware Overview: Electronics Rack
+
+
Electronics Rack
Bud Industries 35RU Rack
Electronics Rack Exoskeleton
Misumi frame.
Insulative Paneling
Bent aluminum sheet metal components lined with insulative foam.

## Slide 5: Hardware Overview: Electronics Rack
Fan Tray
Manufactured by Kooltronic, the fan tray is comprised of 9X 120mm fans capable of 945CFM. It sits atop the heat exchanger and draws air upwards.
Heat Exchanger
Manufactured by Thermatron, the heat exchanger is comprised of a network of 0.375” copper tubes with two parallel paths. The tubes zig zag a total of 20 times which creates a high surface area grid.
Subsystems
All of the support electronics for the various subsystems throughout the telescope sit in the rack mounted shelves or are rack mountable modules.

## Slide 6: Hardware Overview: Electronics Rack
Main Panels
The main panels are made from 0.0625” thick aluminum sheet and are lined with 2”thick insulative adhesive-backed foam. There is one panel on the tube-side of the telescope and one on the outward facing side.
Cable Trays
The electronics rack is equipped with 2X cable trays on either side for managing the electrical cabling and plumbing.
Access Panels
The access panels are made from 0.0625” thick aluminum sheet and lined with 1” thick adhesive-backed foam. The access panels are on either side of the rack and hinge downward when the telescope is at South stow position. They provide convenient access to the various component trays in the rack
Misumi Rail Covers
Bent aluminum sheetmetal lined with 0.5” thick rigid insulation

## Slide 7: Hardware Overview: Electronics Rack
Fan Tray Circulates Air
  The fan tray draws air from the inside of the rack upwards. The air hits the top of the rack and follows the path of least resistance (2 slots out the sides). From the increased pressure, the air is forced down the sides of the rack between the insulative foam on the panels and some panels that form a channel (not shown). The air exists into the main body of the rack through two slots in the bottom and repeats the cycle.
Natural Convection
  The typical orientation of the rack is vertical (or nearly vertical). From natural convection and with the assistance of the fan tray, hot air rises to the top of the rack.
Foamcore Panels
Cool Air Buffer

## Slide 8: Hardware Overview: Archon Controllers
Archon Controllers
The Archon Controllers mount to the telescope with a bent aluminum sheet metal bracket. Each Archon can be conveniently removed from the bracket with 4 screws. The Archons mount outside the telescope tube at the base of the camera support structure legs (4 Archons for the science CCDs and 1 Archon for the guide-focus CCDs)
Coldplate
Each Archon is equipped with a Lytron CP15G01 cold plate which draws heat from the motherboard plane. The coldplate was modified with a threaded hole pattern such that it could be bolted securely to the motherboard plane and have solid thermal conduction.

## Slide 9: Heat Dissipation
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Combination
Rough Circuit Analysis
  Combination Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 10: Heat Dissipation: Required Flow
Electronics Rack:
  Electronics Rack + KUKA Sunrise Cabinet + Guide-Focus Archon – 4(Science Archons)
    513W + 150W +25W - 4(75W) = 388W
Archon Controller: 75W Each
    /Archon
    NO CONDENSATION FROM LINES OR HEAT EXCHANGERS!

## Slide 11: Cooling Equipment Specifications
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Combination
Rough Circuit Analysis
  Combination Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 12: Cooling Equipment Specs: Chiller
Manufacturer: OptiTemp
Model Number: OTC-1.0 with 0.5Hp Pump
Maximum Working Pressure: 90ft (37psi) @6GPM
Chart: Chiller Supply vs Flow Rate
| 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5
Chiller | 45.951 | 45.084 | 44.217 | 43.35 | 42.483 | 41.616 | 40.749 | 39.882 | 39.015 | 38.148 | 37.281 | 36.414

## Slide 13: Cooling Equipment Specs: Electronics Rack Heat Exchanger
Manufacturer: Thermatron
Model Number: 726
Pressure Drop Plot is shown with water at 20C
Chart: E-Rack HX: Pressure Drop vs Flow Rate
| 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5
E-Rack HX | 0.6 | 2.4 | 5.4 | 8.4 | 13.2 | 17.7 | 22.8 | 28.8 | 38.4

## Slide 14: Cooling Equipment Specs: Archon Controller Heat Exchanger
Manufacturer: Lytron
Model Number: CP15G01
Pressure Drop Plot is shown with water at 20C
Chart: Archon HX: Pressure Drop vs Flow Rate
| 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1.1000000000000001 | 1.2 | 1.3
Archon HX (1X) | 0.3 | 1 | 1.5 | 2 | 3 | 3.8 | 4.8 | 6 | 7 | 9 | 11.5 | 17 | 25

## Slide 15: Plumbing Schemes
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Combination
Rough Circuit Analysis
  Combination Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 16: Plumbing Schemes: Serial
Main Supply Line
ID: 0.75”
Length: 50ft
Main Return Line
ID: 0.75”
Length: 50ft
Electronics Rack Heat Exchanger
Thermatron 726 Model
Chiller
OptiTemp OTC-1.0
Archon Supply Branch
ID: 0.27
Length: 6ft
Archon Return Branch
ID: 0.27
Length: 6ft
Advantages:
  Simple plumbing
Disadvantages:
  Big pressure drop
  Considerable temperature difference between Archons

## Slide 17: Plumbing Schemes: Parallel
Main Supply Line
ID: 0.75”
Length: 50ft
Main Return Line
ID: 0.75”
Length: 50ft
Electronics Rack Heat Exchanger
Thermatron 726 Model
Chiller
OptiTemp OTC-1.0
Archon Supply Branch (QTY 2)
ID: 0.270
Length: 6ft
Archon Return Branch (QTY 2)
ID: 0.270
Length: 6ft
Advantages:
  Uniform temperature for all Archons
Disadvantages:
  Complicated plumbing scheme

## Slide 18: Plumbing Schemes: Series-Parallel (not too hot, not too cold)
Main Supply Line
ID: 0.75”
Length: 50ft
Main Return Line
ID: 0.75”
Length: 50ft
Chiller
OptiTemp OTC-1.0
Flow: 1-10GPM @34psi
Archon Supply Branch 1
ID: 0.270
Length: 6ft
Archon Supply Branch 2
ID: 0.270
Length: 10ft
Archon Return Branch 2
ID: 0.270
Length: 10ft
Archon Return Branch 1
ID: 0.270
Length: 6ft

## Slide 19: Rough Circuit Analysis
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Series-Parallel
Rough Circuit Analysis
  Series-Parallel Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 20: Rough Circuit Analysis: Series Parallel
36.5psi
6.5GPM
Assuming 6.5GPM ∆P = 36.5psi = ∆P3+ ∆P4+ ∆P5
Neglecting the pressure drop in the lines, it is assumed all 36.5psi makes it to this branch of the Archon Heat Exchangers. Since each heat exchanger is identical, the pressure drop across each is equivalent (12.1psi). the max flow rate can be ~1.2gpm (see plot).
Assuming 6.5GPM ∆P = ∆PE = 36.5psi
Neglecting the pressure drop in the lines, it is assumed all 36.5psi makes it to this branch of the Rack Heat Exchanger and the resultant flow is ~4.5gpm.
Assuming 6.5GPM ∆P = 36.5psi = ∆P1+ ∆P2
Neglecting the pressure drop in the lines, it is assumed all 36.5psi makes it to this branch of the Archon Heat Exchangers. Since each heat exchanger is identical, the pressure drop across each is equivalent (18.25psi). the max flow rate can be ~1.3gpm (see plot).
Good initial estimates, but what about loss in lines?
Parallel:
Q = Q1 + Q2 + Q3
∆P1 = ∆P2 = ∆P3
Serial:
Q1 = Q2 = Q3
∆P = ∆P1 + ∆P2 + ∆P3

## Slide 21: Circuit Analysis
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Combination
Rough Circuit Analysis
  Combination Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 22: Circuit Analysis: Main Lines
Darcy-Weisbach Equation for Turbulent Flow
  f: Friction Factor (Surface Roughness)
  L: Length of Line
  D: Diameter of Line
  : Density
  v: Flow velocity
  Q: Flow Rate
Main Line Diameter [in] | 0.75
Main Line Length [ft] | 170
Non-negligible pressure drop
Chart: Main Line: Pressure Drop vs Flow Rate
| 2.6 | 3.1 | 3.6 | 4.0999999999999996 | 4.5999999999999996 | 5.0999999999999996 | 5.6 | 6.1 | 6.6 | 7.1 | 7.6 | 8.1
Main Line | 1.6414 | 2.3334 | 3.1469 | 4.0817 | 5.138 | 6.3156 | 7.6147 | 9.0351 | 10.577 | 12.2403 | 14.025 | 15.9311

## Slide 23: Circuit Analysis: Archon Lines
Darcy-Weisbach Equation for Turbulent Flow
  f: Friction Factor (Surface Roughness)
  L: Length of Line
  D: Diameter of Line
  : Density
  v: Flow velocity
  Q: Flow Rate
Archon Line Diameter [in] | 0.25
Archon Branch 1 Line Length [ft] | 12
Archon Branch 2 Line Length [ft] | 20
Still Non-negligible pressure drop
Chart: Archon Lines: Pressure Drop vs Flow Rate
| 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1.1000000000000001 | 1.2 | 1.3
Archon Line 1 (12ft) | 0.028346 | 0.11338 | 0.25512 | 0.45354 | 0.70865 | 1.0205 | 1.389 | 1.8142 | 2.296 | 2.8346 | 3.4299 | 4.0818 | 4.7905
Archon Line 2 (20ft) | 0.047244 | 0.18897 | 0.42519 | 0.7559 | 1.1811 | 1.7008 | 2.3149 | 3.0236 | 3.8267 | 4.7244 | 5.7165 | 6.8031 | 7.9842

## Slide 24: Circuit Analysis: Main Lines + E-Rack HX
Chart: E-Rack Branch: Pressure Drop vs Flow Rate
| 2.6 | 3.1 | 3.6 | 4.0999999999999996 | 4.5999999999999996 | 5.0999999999999996 | 5.6 | 6.1 | 6.6 | 7.1 | 7.6 | 8.1
Main Line + 2.1gpm Archon | 1.6414 | 2.3334 | 3.1469 | 4.0817 | 5.138 | 6.3156 | 7.6147 | 9.0351 | 10.577 | 12.2403 | 14.025 | 15.9311
Chiller Supply | 45.951 | 45.084 | 44.217 | 43.35 | 42.483 | 41.616 | 40.749 | 39.882 | 39.015 | 38.148 | 37.281 | 36.414
E-Rack HX | 0.6 | 2.4 | 5.4 | 8.4 | 13.2 | 17.7 | 22.8 | 28.8 | 38.4
E-Rack + Main Line | 2.2414 | 4.7334 | 8.5469 | 12.4817 | 18.338 | 24.0156 | 30.4147 | 37.8351 | 48.977
2.1GPM was assigned to the Archon paths.
Total Flow: 6.1GPM
  4GPM through E-Rack HX
  2.1GPM through Archons.
  9psi loss in Main Line
9psi
Chiller Operating Pressure

## Slide 25: Circuit Analysis: Main Lines + Archon Lines + Archon HX
Chart: Archon Branch 1: Pressure Drop vs Flow Rate
| 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1.1000000000000001 | 1.2 | 1.3
Archon Line | 0.028346 | 0.11338 | 0.25512 | 0.45354 | 0.70865 | 1.0205 | 1.389 | 1.8142 | 2.296 | 2.8346 | 3.4299 | 4.0818 | 4.7905
Archon Heat Exchanger (2X) | 0.6 | 2 | 3 | 4 | 6 | 7.6 | 9.6 | 12 | 14 | 18 | 23 | 34 | 50
Total | 0.62835 | 2.1134 | 3.2551 | 4.4535 | 6.7087 | 8.6205 | 10.989 | 13.8142 | 16.296 | 20.8346 | 26.4299 | 38.0818 | 54.7905
Branch | Flow [GPM]
E-Rack Branch | 4
Archon Branch 1 | 1.15
Archon Branch 2 | 0.95
Total | 6.1
Chart: Archon Branch 2: Pressure Drop vs Flow Rate
| 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1.1000000000000001 | 1.2 | 1.3
Archon Line | 0.047244 | 0.18897 | 0.42519 | 0.7559 | 1.1811 | 1.7008 | 2.3149 | 3.0236 | 3.8267 | 4.7244 | 5.7165 | 6.8031 | 7.9842
Archon Heat Exchanger (3X) | 0.9 | 3 | 4.5 | 6 | 9 | 11.4 | 14.4 | 18 | 21 | 27 | 34.5 | 51 | 75
Total | 0.94724 | 3.189 | 4.9252 | 6.7559 | 10.1811 | 13.1008 | 16.7149 | 21.0236 | 24.8267 | 31.7244 | 40.2165 | 57.8031 | 82.9842
Plus Main Line ΔP 9psi

## Slide 26: Circuit Analysis: Summary
∆P = 4.5psi
∆P = 4psi
∆P = 29psi, @4GPM
∆P = 9psi
∆P = 24.5psi, 0.95GPM
∆P = 25psi @ 1.15GPM

## Slide 27: Thermal Performance
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Combination
Rough Circuit Analysis
  Combination Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 28: Thermal Performance: Archon Controllers
(Branch 1) @ 1.15GPM
0.0095 (Branch 2) @ 0.95GPM
Heat load is 75W
Branch 1 (2 Archons)
Branch 2 (3 Archons)
    Where

## Slide 29: Thermal Performance: E-Rack HX

## Slide 30: Thermal Performance: Fluid Temp Rise
∆T = 1.4°C, @4GPM
∆T = 2.1°C, 0.95GPM
∆T = 1.27°C @ 1.15GPM

## Slide 31: Thermal Performance: Electronics Rack Air Temperature
Air Flow:
  The fan tray can output 950CFM maximum, so assuming ~40% efficiency, the flow is roughly 400CFM. (Component Obstruction)
PGW (Propylene Glycol Water) Flow:
  4gpm
Thermal Performance:
  For 20C Ambient:
    Coolant is 20C-3C = 17C
    Air is 20C + 5C = 25C
  Heat load is 388W
    Where
Notes:
  Diminishing returns with increased coolant flow
  Save space in the bottom of the rack for another fan set (air flow booster).

## Slide 32: Thermal Performance: Electronics Rack Surface Temperature
  : Stefan-Boltzmann Constant,
  k: Thermal Conductivity
  Ti: Internal Side Insulation Surface Temperature
  Te: Panel Surface Temperature
  Ta: Ambient Temperature
Electronics Rack Surface Temperature:
  Allowed Ti-Te = 12deg
Te
Ta
Ti
Chart: ERack Surface Temperature vs Ambient Temperature
| 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35
T_a = 273K | 0 | 0.45222 | 0.9024 | 1.3506 | 1.7968 | 2.241 | 2.6832 | 3.1236
T_a = 285K | 0 | 0.402 | 0.80245 | 1.2014 | 1.5987 | 1.9946 | 2.3889 | 2.7818
T_a = 295K | 0 | 0.36547 | 0.72968 | 1.0926 | 1.4544 | 1.8149 | 2.1742 | 2.5323
T_a = 305K | 0 | 0.33307 | 0.66513 | 0.99617 | 1.3262 | 1.6553 | 1.9833 | 2.3104

## Slide 33: Plumbing Hardware
Hardware Overview
  What equipment? Where is it located?
  Why do we need to cool it?
Heat Dissipation
  Measured Power
  Required Flow Calculations
Cooling Equipment Specifications
  Chiller
  Electronics Rack Heat Exchanger
  Archon Controller Heat Exchanger
Plumbing Schemes
  Serial
  Parallel
  Combination
Rough Circuit Analysis
  Combination Plumbing Scheme
Circuit Analysis
  Main Lines
  Archon Lines
  E-Rack HX
  Archon HX
Thermal Performance
  Electronics Rack
  Archon Controllers
  Surface Temperature
Plumbing Hardware

## Slide 34: Plumbing Hardware
Archon Plumbing:
QDCs stem and body shutoffs
PTFE lined SS braided hoses
Main Line Plumbing
Parker QDCs
Parker flexible line

## Slide 35: Conclusions
These are theoretical calculations
  Will need to be confirmed through testing
All calculations made at 20C.
  Pressure drops will increase with increased viscosity.
Fluid flow pressure drops are non-linear. Not as easy as electrical engineering
  Electrical Engineering is easier than Plumbing