## Update Info
File: | KAON 753 Safety System Interface Control Spreadsheet
Purpose: | ICD to describe interface between the Safety PLC, AKCP servers, the hardware, and the software
Updates | April 08, 2010, Initial PD Release | JChin
| May 04, 2010; updated KAON # | JChin

## PLC Interface
Interfaces of the Safety System
Laser1 | From |  | To | Type | Scale | Level | Node | Input Board | Slot | Point | Terminal Block | Connector | Connector Pin | Word # | S/W Bit
24VDC | SS | -> | Laser1 | Digital | 24VDC | DC | AO |  |  |  | TB3 | Laser1 | P1-A
COM | SS | -> | Laser1 | Digital | COM | DC | AO |  |  |  | TB3 | Laser1 | P1-B
Laser1 Emergency Shutdown | SS | -> | Laser1 | Digital | 24VDC | 0 to stop any light generation | AO | 1746-OB32 | 6 | 0 | TB-4- 0 | Laser1 | P1-C | Output0 | 0
Laser1 Emergency Power Shutdown | SS | -> | Laser1 | Digital | 24VDC | 0 to shut all power | AO | 1746-OB32 | 6 | 1 | TB-4- 1 | Laser1 | P1-D | Output0 | 1
Laser1 Output Shutter Permissive | SS | -> | Laser1 | Digital | 24VDC | 1 to allow shutter to open | AO | 1746-OB32 | 6 | 2 | TB-4- 2 | Laser1 | P1-E | Output0 | 2
Laser1 Emission ON | Laser1 | -> | SS | Digital | 24VDC | 1 if Laser generating laser light | AO | 1746-IB32 | 3 | 0 | TB-1- 0 | Laser1 | P1-F | Input0 | 0
Laser1 Safety Status | Laser1 | -> | SS | Digital | 24VDC | 0 if an internal fault exists | AO | 1746-IB32 | 3 | 1 | TB-1- 1 | Laser1 | P1-G | Input0 | 1
Laser1 Output Shutter Closed | Laser1 | -> | SS | Digital | 24VDC | 1 if shutter is closed | AO | 1746-IB32 | 3 | 2 | TB-1- 2 | Laser1 | P1-H | Input0 | 2
Laser1 Output Shutter Fault | Laser1 | -> | SS | Digital | 24VDC | 0 if there is a fault of the shutter | AO | 1746-IB32 | 3 | 3 | TB-1- 3 | Laser1 | P1-J | Input0 | 3
Laser1 Exposed Radiation | Laser1 | -> | SS | Digital | 24VDC | 0 if there is exposed radiation | AO | 1746-IB32 | 3 | 4 | TB-1- 4 | Laser1 | P1-K | Input0 | 4
Laser1 System Fault | Laser1 | -> | SS | Digital | 24VDC | 0 if there is an internal fault | AO | 1746-IB32 | 3 | 5 | TB-1- 5 | Laser1 | P1-L | Input0 | 5
Laser1 Interface Fault | Laser1 | -> | SS | Digital | 24VDC | 0 if there is an interface fault | AO | 1746-IB32 | 3 | 6 | TB-1- 6 | Laser1 | P1-M | Input0 | 6
Laser2 | From |  | To | Type | Scale | Level
24VDC | SS | -> | Laser1 | Digital | 24VDC | DC | AO |  |  |  | TB3 | Laser2 | P2-A
COM | SS | -> | Laser1 | Digital | COM | DC | AO |  |  |  | TB3 | Laser2 | P2-B
Laser2 Emergency Shutdown | SS | -> | Laser2 | Digital | 24VDC | 0 to stop any light generation | AO | 1746-OB32 | 6 | 4 | TB-4- 4 | Laser2 | P2-C | Output 0 | 4
Laser2 Emergency Power Shutdown | SS | -> | Laser2 | Digital | 24VDC | 0 to shut all power | AO | 1746-OB32 | 6 | 5 | TB-4- 5 | Laser2 | P2-D | Output 0 | 5
Laser2 Output Shutter Permissive | SS | -> | Laser2 | Digital | 24VDC | 1 to allow shutter to open | AO | 1746-OB32 | 6 | 6 | TB-4- 6 | Laser2 | P2-E | Output 0 | 6
Laser2 Emission ON | Laser2 | -> | SS | Digital | 24VDC | 1 if Laser generating laser light | AO | 1746-IB32 | 3 | 8 | TB-1- 8 | Laser2 | P2-F | Input0 | 7
Laser2 Safety Status | Laser2 | -> | SS | Digital | 24VDC | 0 if an internal fault exists | AO | 1746-IB32 | 3 | 9 | TB-1- 9 | Laser2 | P2-G | Input0 | 8
Laser2 Output Shutter Closed | Laser2 | -> | SS | Digital | 24VDC | 1 if shutter is closed | AO | 1746-IB32 | 3 | 10 | TB-1- 10 | Laser2 | P2-H | Input0 | 9
Laser2 Output Shutter Fault | Laser2 | -> | SS | Digital | 24VDC | 0 if there is a fault of the shutter | AO | 1746-IB32 | 3 | 11 | TB-1- 11 | Laser2 | P2-J | Input0 | 10
Laser2 Exposed Radiation | Laser2 | -> | SS | Digital | 24VDC | 0 if there is exposed radiation | AO | 1746-IB32 | 3 | 12 | TB-1- 12 | Laser2 | P2-K | Input0 | 11
Laser2 System Fault | Laser2 | -> | SS | Digital | 24VDC | 0 if there is an internal fault | AO | 1746-IB32 | 3 | 13 | TB-1- 13 | Laser2 | P2-L | Input0 | 12
Laser2 Interface Fault | Laser2 | -> | SS | Digital | 24VDC | 0 if there is an interface fault | AO | 1746-IB32 | 3 | 14 | TB-1- 14 | Laser2 | P2-M | Input0 | 13
Laser3 | From |  | To | Type | Scale | Level
24VDC | SS | -> | Laser1 | Digital | 24VDC | DC | AO |  |  |  | TB3 | Laser3 | P3-A
COM | SS | -> | Laser1 | Digital | COM | DC | AO |  |  |  | TB3 | Laser3 | P3-B
Laser3 Emergency Shutdown | SS | -> | Laser3 | Digital | 24VDC | 0 to stop any light generation | AO | 1746-OB32 | 6 | 8 | TB-4- 8 | Laser3 | P3-C | Output 0 | 8
Laser3 Emergency Power Shutdown | SS | -> | Laser3 | Digital | 24VDC | 0 to shut all power | AO | 1746-OB32 | 6 | 9 | TB-4- 9 | Laser3 | P3-D | Output 0 | 9
Laser3 Output Shutter Permissive | SS | -> | Laser3 | Digital | 24VDC | 1 to allow shutter to open | AO | 1746-OB32 | 6 | 10 | TB-4- 10 | Laser3 | P3-E | Output 0 | 10
Laser3 Emission ON | Laser3 | -> | SS | Digital | 24VDC | 1 if Laser generating laser light | AO | 1746-IB32 | 3 | 16 | TB-1- 16 | Laser3 | P3-F | Input1 | 0
Laser3 Safety Status | Laser3 | -> | SS | Digital | 24VDC | 0 if an internal fault exists | AO | 1746-IB32 | 3 | 17 | TB-1- 17 | Laser3 | P3-G | Input1 | 1
Laser3 Output Shutter Closed | Laser3 | -> | SS | Digital | 24VDC | 1 if shutter is closed | AO | 1746-IB32 | 3 | 18 | TB-1- 18 | Laser3 | P3-H | Input1 | 2
Laser3 Output Shutter Fault | Laser3 | -> | SS | Digital | 24VDC | 0 if there is a fault of the shutter | AO | 1746-IB32 | 3 | 19 | TB-1- 19 | Laser3 | P3-J | Input1 | 3
Laser3 Exposed Radiation | Laser3 | -> | SS | Digital | 24VDC | 0 if there is exposed radiation | AO | 1746-IB32 | 3 | 20 | TB-1- 20 | Laser3 | P3-K | Input1 | 4
Laser3 System Fault | Laser3 | -> | SS | Digital | 24VDC | 0 if there is an internal fault | AO | 1746-IB32 | 3 | 21 | TB-1- 21 | Laser3 | P3-L | Input1 | 5
Laser3 Interface Fault | Laser3 | -> | SS | Digital | 24VDC | 0 if there is an interface fault | AO | 1746-IB32 | 3 | 22 | TB-1- 22 | Laser3 | P3-M | Input1 | 6
Laser4 | From |  | To | Type | Scale | Level
24VDC | SS | -> | Laser4 | Digital | 24VDC | DC | AO |  |  |  | TB1- | Laser4 | P4-A
COM | SS | -> | Laser4 | Digital | COM | DC | AO |  |  |  | TB1- | Laser4 | P4-B
Laser4 Emergency Shutdown | SS | -> | Laser4 | Digital | 24VDC | 0 to stop any light generation | AO | 1746-OB32 | 6 | 12 | TB-4- 12 | Laser4 | P4-C | Output 0 | 12
Laser4 Emergency Power Shutdown | SS | -> | Laser4 | Digital | 24VDC | 0 to shut all power | AO | 1746-OB32 | 6 | 13 | TB-4- 13 | Laser4 | P4-D | Output 0 | 13
Laser4 Output Shutter Permissive | SS | -> | Laser4 | Digital | 24VDC | 1 to allow shutter to open | AO | 1746-OB32 | 6 | 14 | TB-4- 14 | Laser4 | P4-E | Output 0 | 14
Laser4 Emission ON | Laser4 | -> | SS | Digital | 24VDC | 1 if Laser generating laser light | AO | 1746-IB32 | 3 | 24 | TB-1- 24 | Laser4 | P4-F | Input1 | 7
Laser4 Safety Status | Laser4 | -> | SS | Digital | 24VDC | 0 if an internal fault exists | AO | 1746-IB32 | 3 | 25 | TB-1- 25 | Laser4 | P4-G | Input1 | 8
Laser4 Output Shutter Closed | Laser4 | -> | SS | Digital | 24VDC | 1 if shutter is closed | AO | 1746-IB32 | 3 | 26 | TB-1- 26 | Laser4 | P4-H | Input1 | 9
Laser4 Output Shutter Fault | Laser4 | -> | SS | Digital | 24VDC | 0 if there is a fault of the shutter | AO | 1746-IB32 | 3 | 27 | TB-1- 27 | Laser4 | P4-J | Input1 | 10
Laser4 Exposed Radiation | Laser4 | -> | SS | Digital | 24VDC | 0 if there is exposed radiation | AO | 1746-IB32 | 3 | 28 | TB-1- 28 | Laser4 | P4-K | Input1 | 11
Laser4 System Fault | Laser4 | -> | SS | Digital | 24VDC | 0 if there is an internal fault | AO | 1746-IB32 | 3 | 29 | TB-1- 29 | Laser4 | P4L | Input1 | 12
Laser4 Interface Fault | Laser4 | -> | SS | Digital | 24VDC | 0 if there is an interface fault | AO | 1746-IB32 | 3 | 30 | TB-1- 30 | Laser4 | P4-M | Input1 | 13
Laser Launch Facility
24VDC | SS | -> | LLF | Digital | 24VDC | DC | AO |  |  |  | TB3 | LLF | P5-A
COM | SS | -> | LLF | Digital | COM | DC | AO |  |  |  | TB3 | LLF | P5-B
LF Status Green | SS | -> | LLF | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 0 | TB-5- 0 | LLF | P5-C | Output1 | 0
LF Status Yellow | SS | -> | LLF | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 1 | TB-5- 1 | LLF | P5-D | Output1 | 1
LF Status Red | SS | -> | LLF | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 2 | TB-5- 2 | LLF | P5-E | Output1 | 2
Final Shutter Command | SS | -> | LLF | Digital | 24VDC | 1=OPEN | AO | 1746-OPB16 | 7 | 3 | TB-5- 3 | LLF | P5-F | Output1 | 3
Fast Shutter Command | SS | -> | LLF | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 11 | TB-5- 11 | LSE1 | P8-H | Output1 | 11
Beam Dump Insertion | SS | -> | LSE1 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 12 | TB-5- 12 | LSE1 | P8-H | Output1 | 12
LF Cover Status | LLF | -> | SS | Digital | 24VDC | Switch Closed = Cabinet Closed | AO | 1746-IB32 | 4 | 0 | TB-2- 0 | LLF | P5-G | Input 2 | 0
LF E-Stop Status | LLF | -> | SS | Digital | 24VDC | Switch Closed = Not Activated | AO | 1746-IB32 | 4 | 1 | TB-2- 1 | LLF | P5-H | Input 2 | 1
Launch Facility Interlock | LLF | -> | SS | Digital | 24VDC | Switch Closed = In Position | AO | 1746-IB32 | 4 | 2 | TB-2- 2 | LLF | P5-J | Input 2 | 2
Final Shutter Closed Status | LLF | -> | SS | Digital | 24VDC | Switch Closed = Shutter NOT Closed | AO | 1746-IB32 | 4 | 3 | TB-2- 3 | LLF | P5-K | Input 2 | 3
Final Shutter Opened Status | LLF | -> | SS | Digital | 24VDC | Switch Closed = Shutter NOT Opened | AO | 1746-IB32 | 4 | 4 | TB-2- 4 | LLF | P5-M | Input 2 | 4
LF Request for Status | LLF | -> | SS | Digital | 24VDC | Switch Closed = Request | AO | 1746-IB32 | 4 | 5 | TB-2- 5 | LLF | P5-N | Input 2 | 5
AGND | SS | -> | LLF | Analog | [8 empty] | P6-A
Beam Position X | LLF | -> | SS | Analog | 0-10VDC | Calibration for 5VDC center | AO | 1746-NI8 | 5 | 0 | TB-6- 0 | LLF | P6-B | Input 5 | 0
Beam Position Y | LLF | -> | SS | Analog | 0-10VDC | Calibration for 5VDC center | AO | 1746-NI8 | 5 | 1 | TB-6- 1 | LLF | P6-C | Input 6 | 1
Beam Power | LLF | -> | SS | Analog | 0-10VDC | Calibration; 10VDC max power | AO | 1746-NI8 | 5 | 2 | TB-6- 2 | LLF | P6-D | Input 7 | 2
Beam Dump Laser Power | LSE1 | -> | SS | Analog | 0-10VDC |  | AO | 1746-NI8 | 5 | 3 | TB-6- 3 | LSE1 | P7-V | Input 8 | 3
Laser Service Enclosure 1
24VDC | SS | -> | LLF | Digital | 24VDC | DC | AO |  |  |  | TB3 | LF | P7-A
COM | SS | -> | LLF | Digital | COM | DC | AO |  |  |  | TB3 | LF | P7-B
LSE1 E-Stop Activated | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Not Activated | AO | 1746-IB32 | 4 | 9 | TB-2- 9 | LSE1 | P7-C | Input 2 | 9
LSE1 SS Reset Activated | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Reset | AO | 1746-IB32 | 4 | 10 | TB-2- 10 | LSE1 | P7-D | Input 2 | 10
LSE1 Door Status | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Door Closed | AO | 1746-IB32 | 4 | 11 | TB-2- 11 | LSE1 | P7-E | Input 2 | 11
LSE1 Laser1 Cabinet Status | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Cabinet Closed | AO | 1746-IB32 | 4 | 12 | TB-2- 12 | LSE1 | P7-F | Input 2 | 12
LSE1 Laser2 Cabinet Status | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Cabinet Closed | AO | 1746-IB32 | 4 | 13 | TB-2- 13 | LSE1 | P7-G | Input 2 | 13
LSE1 Laser3 Cabinet Status | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Cabinet Closed | AO | 1746-IB32 | 4 | 14 | TB-2- 14 | LSE1 | P7-G | Input 2 | 14
LSE1 Smoke Alarm | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 15 | TB-2- 15 | LSE1 | P7-H | Input 2 | 15
LSE1 Glycol Flow | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 16 | TB-2- 16 | LSE1 | P7-N | Input 3 | 0
LSE1 Request for Status | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Request | AO | 1746-IB32 | 4 | 17 | TB-2- 17 | LSE1 | P7-R | Input 3 | 1
Fast Shutter Closed Status | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Shutter NOT Closed | AO | 1746-IB32 | 4 | 18 | TB-2- 18 | LSE1 | P7-T | Input 3 | 2
Fast Shutter Opened Status | LSE1 | -> | SS | Digital | 24VDC | Switch Closed = Shutter NOT Opened | AO | 1746-IB32 | 4 | 19 | TB-2- 19 | LSE1 | P7-U | Input 3 | 3
AGND | SS | -> | LSE1 | Analog |  |  | AO | [5 empty] | P7-Z
LSE1 Door Lock Command | SS | -> | LSE1 | Digital | 24VDC | 24VDC = Unlock | AO | 1746-OPB16 | 7 | 4 | TB-5- 4 | LSE1 | P8-A | Output1 | 4
LSE1 Door Lock Status Blue | SS | -> | LSE1 | Digital | 24VDC | 24VDC = LED ON Unlocked | AO | 1746-OPB16 | 7 | 5 | TB-5- 5 | LSE1 | P8-B | Output1 | 5
LSE1 Audible Alarm | SS | -> | LSE1 | Digital | 24VDC | 24VDC = Alarm | AO | 1746-OPB16 | 7 | 6 | TB-5- 6 | LSE1 | P8-C | Output1 | 6
LSE1 Status Green | SS | -> | LSE1 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 7 | TB-5- 7 | LSE1 | P8-D | Output1 | 7
LSE1 Status Yellow | SS | -> | LSE1 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 8 | TB-5- 8 | LSE1 | P8-E | Output1 | 8
LSE1 Status Red | SS | -> | LSE1 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 9 | TB-5- 9 | LSE1 | P8-F | Output1 | 9
LSE1 Shunt Trip | SS | -> | LSE1 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OPB16 | 7 | 10 | TB-5- 10 | LSE1 | P8-G | Output1 | 10
Laser Service Enclosure 2 (not used)
LSE2 E-Stop Activated | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = Not Activated | AO
LSE2 SS Reset Activated | LSE2 | -> | SS | Momentary Switch | 24VDC | Switch Closed = Reset | AO | 1746-IB32 | 4 | 16 | TB-2- 16 | LSE2 | P7-A | Input3 | 1
LSE2 Door Status | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = Door Closed | AO | 1746-IB32 | 4 | 17 | TB-2- 17 | LSE2 | P7-B | Input3 | 2
LSE2 Laser3 Cabinet Status | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = Cabinet Closed | AO | 1746-IB32 | 4 | 18 | TB-2- 18 | LSE2 | P7-C | Input3 | 3
LSE2 Laser4 Cabinet Status (Spare) | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = Cabinet Closed | AO | 1746-IB32 | 4 | 19 | TB-2- 19 | LSE2 | P7-D | Input3 | 4
LSE2 Fire Alarm | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 20 | TB-2- 20 | LSE2 | P7-E | Input3 | 5
LSE2 Humidity Alarm | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 21 | TB-2- 21 | LSE2 | P7-F | Input3 | 6
LSE2 Room Temperature Alarm | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 22 | TB-2- 22 | LSE2 | P7-G | Input3 | 7
LSE2 Glycol In Temperature Alarm | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 23 | TB-2- 23 | LSE2 | P7-H | Input3 | 8
LSE2 Laser3 Glycol Flow Alarm | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 24 | TB-2- 24 | LSE2 | P7-J | Input3 | 9
LSE2 Laser4 Glycol Flow Alarm (Spare) | LSE2 | -> | SS | Switch | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 4 | 25 | TB-2- 25 | LSE2 | P7-K | Input3 | 10
LSE2 Request for Status | LSE2 | -> | SS | Momentary Switch | 24VDC | Switch Closed = Request | AO | 1746-IB32 | 4 | 26 | TB-2- 26 | LSE2 | P7-M | Input3 | 11
LSE2 Environmental System Status | LSE2 | -> | SS | Digital | 24VDC | Switch Closed = Not Faulted | AO | 1746-IB32 | 4 | 27 | TB-2- 27 | LSE2 | P7-N | Input3 | 12
LSE2 Door Lock Command | SS | -> | LSE2 | Digital | 24VDC | 24VDC = Unlock | AO | 1746-IB32 | 4 | 28 | TB-2- 28 | LSE2 | P7-P | Input3 | 13
LSE2 Door Lock Status Blue | SS | -> | LSE2 | Digital | 24VDC | 24VDC = LED ON Unlocked | AO | 1746-OB32 | 6 | 20 | TB-4- 20 | LSE2 | P7-R | Output1 | 8
LSE2 Audible Alarm | SS | -> | LSE2 | Digital | 24VDC | 24VDC = Alarm | AO | 1746-OB32 | 6 | 21 | TB-4- 21 | LSE2 | P7-S | Output1 | 9
LSE2 Status Green | SS | -> | LSE2 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OB32 | 6 | 22 | TB-4- 22 | LSE2 | P7-T | Output1 | 10
LSE2 Status Yellow | SS | -> | LSE2 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OB32 | 6 | 23 | TB-4- 23 | LSE2 | P7-U | Output1 | 11
LSE2 Status Red | SS | -> | LSE2 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OB32 | 6 | 24 | TB-4- 24 | LSE2 | P7-V | Output1 | 12
LSE2 Shunt Trip | SS | -> | LSE2 | Digital | 24VDC | 24VDC = LED ON | AO | 1746-OB32 | 6 | 25 | TB-4- 25 | LSE2 | P7-W | Output1 | 13
[8 empty] | 1746-OB32 | 6 | 26 | TB-4- 26 | LSE2 | P7-X | Output1 | 14
Adaptive Optics Faciity (maybe handle outside of SS)
AOF Temperature Alarm | AOF | -> | SS | Digital | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 5 | 0 | TB-3- 0 | Local | - | Input4 | 0
AOF Glycol Temperature Alarm | AOF | -> | SS | Digital | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 5 | 1 | TB-3- 1 | Local | - | Input4 | 1
AOF Glycol Flow Alarm | AOF | -> | SS | Digital | 24VDC | Switch Closed = No Alarm | AO | 1746-IB32 | 5 | 2 | TB-3- 2 | Local | - | Input4 | 2
AOF Shunt Trip | SS | -> | SS | Digital | 24VDC | Switch Closed = Activation | AO | 1746-OB32 | 6 | 27 | TB-4- 27 | Local | - | Output1 | 15
Facility / Aircraft Detection
24VDC | SS | -> | FAC/AD | Digital | 24VDC | DC | AO |  |  |  | TB3 | FAC/AD | P9-A
COM | SS | -> | FAC/AD | Digital | COM | DC | AO |  |  |  | TB3 | FAC/AD | P9-B
Facility E-Stop Activated | FAC | -> | SS | Switch | 24VDC | 24VDC = Not active | CR | 1746-IB32 | 4 | 24 | TB-2- 24 | FAC/AD | P9-C | Input 3 | 8
East Spotter Connected | AD | -> | SS | Switch | 24VDC | 24VDC = Connected | CR | 1746-IB32 | 4 | 25 | TB-2- 25 | FAC/AD | P9-D | Input 3 | 9
East Spotter Activated | AD | -> | SS | Switch | 24VDC | 24VDC = No Detection | CR | 1746-IB32 | 4 | 26 | TB-2- 26 | FAC/AD | P9-E | Input 3 | 10
West Spotter Connected | AD | -> | SS | Switch | 24VDC | 24VDC = Connected | CR | 1746-IB32 | 4 | 27 | TB-2- 27 | FAC/AD | P9-F | Input 3 | 11
West Spotter Activated | AD | -> | SS | Switch | 24VDC | 24VDC = No Detection | CR | 1746-IB32 | 4 | 28 | TB-2- 28 | FAC/AD | P9-G | Input 3 | 12
24VDC | SS | -> | FAC/AD | Digital | 24VDC | DC | AO |  |  |  | TB3 | FAC/AD | P9-H
COM | SS | -> | FAC/AD | Digital | COM | DC | AO |  |  |  | TB3 | FAC/AD | P9-J
Dome Status Green | SS | -> | LF | Digital | 24VDC | 24VDC = LED ON | CR | 1746-OPB16 | 7 | 13 | TB-5- 13 | FAC/AD | P9-K | Ouput 1 | 13
Dome Status Yellow | SS | -> | LF | Digital | 24VDC | 24VDC = LED ON | CR | 1746-OPB16 | 7 | 14 | TB-5- 14 | FAC/AD | P9-M | Ouput 1 | 14
Dome Status Red | SS | -> | LF | Digital | 24VDC | 24VDC = LED ON | CR | 1746-OPB16 | 7 | 15 | TB-5- 15 | FAC/AD | P9-N | Ouput 1 | 15
Laser Interface System
Communications | LIS | <--> | SS | Serial RS232 or Ethernet
LIS Hearbeat | LIS | -> | SS | Software | 16-bit word | 1-300 | [7 empty] | In0
SS Heartbeat | SS | -> | LIS | Software | 16-bit word | 1-300 | [7 empty] | In1
Drive and Control Permissive | LIS | -> | SS | Software | Level | 1=Permissive | [7 empty] | In2 | 0
Observing Assistant Permissive | LIS | -> | SS | Software | Level | 1=Permissive | [7 empty] | In2 | 1
Laser Traffic Control System Permissive | LIS | -> | SS | Software | Level | 1=Permissive | [7 empty] | In2 | 2
Satellites Permissive | LIS | -> | SS | Software | Level | 1=Permissive | [7 empty] | In2 | 3
Elevation Limit Permissive | LIS | -> | SS | Software | Level | 1=Permissive | [7 empty] | In2 | 4
Laser E-Stop Command | LIS | -> | SS | Software | Level | 1=Activate E-STOP | [7 empty] | In2 | 6
Open Final Shutter Command | LIS | -> | SS | Software | Edge | Rising Edge = Open; 0 =Close | [7 empty] | In2 | 7
Open Fast Shutter Command | LIS | -> | SS | Software | Edge | Rising Edge = Open; 0 =Close | [7 empty] | In2 | 8
Reset SS Fault Status | LIS | -> | SS | Software | Edge | Rising Edge = Clear | [7 empty] | In2 | 9
SS Heartbeat Interface Fault Latch | LIS | -> | SS | Software | Level | 1= Latched | [7 empty] | In2 | 10
Facility E-Stop Activated Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out0 | 0
Laser E-Stop Activated Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out0 | 1
Programmable Logic Controller Fault | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out0 | 2
LSE1 Smoke Alarm Activated Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 0
LSE1 Glycol Flow Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 1
LSE1 Beam Interlock Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 7
LSE2 Smoke Alarm Activated Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 7
LSE2 Laser3 Glycol Flow Low Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 8
LSE2 Laser4 Glycol Flow Low Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 9
LSE2 Glycol In Temp Alarm Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 10
LSE2 Room Temp Alarm Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 11
LSE2 Humidity Alarm Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 12
LSE2 Beam Interlock Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out1 | 13
East Spotter Activated Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 0
West Spotter Activated Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 1
East Spotter Disconnected Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 2
West Spotter Disconnected Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 3
DCS Permissive Dropped while Propagating Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 4
LTCS Permissive Dropped while Propagating Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 5
Satellite Permissive Dropped while Propagating Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 7
Elevation Permissive Dropped while Propagating Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out2 | 9
Laser1 Safety Status Failed Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 0
Laser1 Output Shutter Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 1
Laser2 Safety Status Failed Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 2
Laser2 Output Shutter Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 3
Laser3 Safety Status Failed Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 4
Laser3 Output Shutter Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 5
Laser4 Safety Status Failed Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 6
Laser4 Output Shutter Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out3 | 7
LF Final Shutter Faulted Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out4 | 0
LF Fast Shutter Faulted Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out4 | 1
LF Beam Misalignment Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out4 | 2
LF Beam Power Low Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out4 | 3
LF Beam Interlock Fault Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out4 | 4
LF Temperature Alarm Latch | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out4 | 5
LF Final Shutter Permissive | SS | -> | LIS | Software | Level | 1=Permissive | [7 empty] | Out4 | 6
LF Final Shuter Status | SS | -> | LIS | Software | Level | 1= Latched | [7 empty] | Out4 | 7
LF Fast Shutter Permissive | SS | -> | LIS | Software | Level | 1=Permissive | [7 empty] | Out4 | 8
LF Fast Shutter Status | SS | -> | LIS | Software | Level | 1=Open | [7 empty] | Out4 | 9
Propagating On Sky | SS | -> | LIS | Software | Level | 1=On Sky Propagatin | [7 empty] | Out4 | 10
SS Internal I/O
Computer Room Node
CR Laser E-Stop Activation | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = Not Activated | CR | 1746-IB32 | 3 | 16 | TB-1- 16 | Local | - | CRI2 | 0
CR SS Fault Reset | CR | -> | CR PLC | Momentary Switch | 24VDC | Switch Closed = Reset | CR | 1746-IB32 | 3 | 17 | TB-1- 17 | Local | - | CRI2 | 1
User Mode 1 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 18 | TB-1- 18 | Local | - | CRI2 | 2
User Mode 2 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 19 | TB-1- 19 | Local | - | CRI2 | 3
User Mode 3 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 20 | TB-1- 20 | Local | - | CRI2 | 4
User Mode 4 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 21 | TB-1- 21 | Local | - | CRI2 | 5
Bypass Mode 1 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 22 | TB-1- 22 | Local | - | CRI2 | 6
Bypass Mode 2 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 23 | TB-1- 23 | Local | - | CRI2 | 7
Bypass Mode 3 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 24 | TB-1- 24 | Local | - | CRI2 | 8
Bypass Mode 4 | CR | -> | CR PLC | Switch | 24VDC | Switch Closed = | CR | 1746-IB32 | 3 | 25 | TB-1- 25 | Local | - | CRI2 | 9
LED Status 1 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 0 | TB-2- 0 | Local | - | CR01 | 0
LED Status 2 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 1 | TB-2- 1 | Local | - | CR01 | 1
LED Status 3 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 2 | TB-2- 2 | Local | - | CR01 | 2
LED Status 4 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 3 | TB-2- 3 | Local | - | CR01 | 3
LED Status 5 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 4 | TB-2- 4 | Local | - | CR01 | 4
LED Status 6 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 5 | TB-2- 5 | Local | - | CR01 | 5
LED Status 7 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 6 | TB-2- 6 | Local | - | CR01 | 6
LED Status 8 | CR PLC | -> | CR | LED | 24VDC | 24VDC = ON | CR | 1746-OB32 | 4 | 7 | TB-2- 7 | Local | - | CR01 | 7
Adaptive Optics Node
AO Laser E-Stop Activation | AO | -> | AO Remote | Switch | 24VDC | Switch Closed = Not Activated | AO | 1746-IB32 | 5 | 8 | TB-3- 8 | Local | - | Input4 | 8
AO SS Fault Reset | AO | -> | AO Remote | Momentary Switch | 24VDC | Switch Closed = Reset | AO | 1746-IB32 | 5 | 9 | TB-3- 9 | Local | - | Input4 | 9
LED Status 1 | AO Remote | -> | AO | LED | 24VDC | 24VDC = ON | AO | 1746-OB32 | 6 | 28 | TB-4- 28 | Local | - | Output2 | 0
LED Status 2 | AO Remote | -> | AO | LED | 24VDC | 24VDC = ON | AO | 1746-OB32 | 6 | 29 | TB-4- 29 | Local | - | Output2 | 1
LED Status 3 | AO Remote | -> | AO | LED | 24VDC | 24VDC = ON | AO | 1746-OB32 | 6 | 30 | TB-4- 30 | Local | - | Output2 | 2
LED Status 4 | AO Remote | -> | AO | LED | 24VDC | 24VDC = ON | AO | 1746-OB32 | 6 | 31 | TB-4- 31 | Local | - | Output2 | 3
*Spare

## AKCP Server
Interfaces to AKCP Server
AO Server | From |  | To | Type | Scale | Sensor # | Cable | Word # | S/W Bit
Temperature 1 | AOE | -> | AK1 | Intel Sensor | 1C | 1 | AK1-IS - 1 | 0
Temperature 2 | AOE | -> | AK1 | Intel Sensor | 1C | 2 | AK1-IS - 2 | 1
Temperature 3 | AOE | -> | AK1 | Intel Sensor | 1C | 3 | AK1-IS - 3 | 2
Temperature 4 | AOE | -> | AK1 | Intel Sensor | 1C | 4 | AK1-IS - 4 | 3
Humidity 1 | AOE | -> | AK1 | Intel Sensor | 1% | 5 | AK1-IS - 5 | 4
Humidity 2 | AOE | -> | AK1 | Intel Sensor | 1% | 6 | AK1-IS - 6 | 5
Spare 1 | AOE | -> | AK1 | Intel Sensor | 1% | 7 | AK1-IS - 7 | 6
Spare 2 | AOE | -> | AK1 | Intel Sensor | 1% | 8 | AK1-IS - 8 | 7
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 1 | AK1-IS - 1 | 8 | 0
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 2 | AK1-IS - 2 | 8 | 1
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 3 | AK1-IS - 3 | 8 | 2
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 4 | AK1-IS - 4 | 8 | 3
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 5 | AK1-IS - 5 | 8 | 4
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 6 | AK1-IS - 6 | 8 | 5
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 7 | AK1-IS - 7 | 8 | 6
Spare D I/O | AOE | < -> | AK1 | Dry contact | On/Off | 8 | AK1-IS - 8 | 8 | 7
Laser Server
Temperature 1 | LSE | -> | AK2 | Intel Sensor | 1C | 1 | AK2-IS - 1 | 0
Temperature 2 | LSE | -> | AK2 | Intel Sensor | 1C | 2 | AK2-IS - 2 | 1
Temperature 3 | LSE | -> | AK2 | Intel Sensor | 1C | 3 | AK2-IS - 3 | 2
Temperature 4 | LSE | -> | AK2 | Intel Sensor | 1C | 4 | AK2-IS - 4 | 3
Humidity 1 | LSE | -> | AK2 | Intel Sensor | 1% | 5 | AK2-IS - 5 | 4
Humidity 2 | LSE | -> | AK2 | Intel Sensor | 1% | 6 | AK2-IS - 6 | 5
Spare 1 | LSE | -> | AK2 | Intel Sensor | 1% | 7 | AK2-IS - 7 | 6
Spare 2 | LSE | -> | AK2 | Intel Sensor | 1% | 8 | AK2-IS - 8 | 7
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 1 | AK2-DIO - 1 | 8 | 0
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 2 | AK2-DIO - 2 | 8 | 1
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 3 | AK2-DIO - 3 | 8 | 2
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 4 | AK2-DIO - 4 | 8 | 3
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 5 | AK2-DIO - 5 | 8 | 4
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 6 | AK2-DIO - 6 | 8 | 5
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 7 | AK2-DIO - 7 | 8 | 6
Spare D I/O | LSE | < -> | AK2 | Dry contact | On/Off | 8 | AK2-DIO - 8 | 8 | 7

## Layout Info
Terminal Block | Board Interface | Channels
TB1 | IB32 | 32
TB2 | IB32 | 32
TB3 | Power/GND
TB4 | OB | 32
TB5 | OPB | 16
TB6 | NI8 | 8
Connector | Subsystem
P1 | Laser1
P2 | Laser2
P3 | Laser3
P4 | Laser4
P5 | LF D
P6 | LF A
P7 | LSE I
P8 | LSE O
P9 | Fac/ACD
PLC | Card
Slot 1 | Power
Slot 2 | Processor
Slot 3 | IB32
Slot 4 | IB32
Slot 5 | NI8
Slot 6 | OB32
Slot 7 | OPB16