## Sheet1
ROOM 21B CLEAN ROOM PARTICLE TRACKING SHEET | [11 empty] | ROOM | AVE | ROOM | AVE
[13 empty] | 0.5um |  | 5.0um
ROOM 21 B | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials |  |  |  | [particles/m^3] |  | [particles/m^3]
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  |  |  | ROOM 21 B | 14285 | ROOM 21 B | 689.75
0.5um | 2015-05-01 | 15100 | 4240 | 12800 | 25000 | 14285 | 8535.8597 | Pass | PEM |  |  | ROOM 21 A | 1192500 | ROOM 21 A | 3195
[particles/m^3] | [11 empty] | ROOM 21 | 977166.6667 | ROOM 21 | 6005
5.0um | 2015-05-01 | 565 | 141 | 353 | 1700 | 689.75 | 695.3883 | Pass | PEM |  |  | ROOM 17 | 728000 | ROOM 17 | 12112.5
[particles/m^3] | [11 empty] | ROOM 15 | 30045 | ROOM 15 | 1624.5
[12 empty] | ROOM 14 | 672000 | ROOM 14 | 2735
ROOM 21A CLEAN ROOM PARTICLE TRACKING SHEET | [11 empty] | ROOM 12 I | 10758.3333 | ROOM 12 I | 977.8333
[12 empty] | ROOM 12 O | 23025 | ROOM 12 O | 1942
ROOM 21 A | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials |  |  | ROOM 10 G | 456500 | ROOM 10 G | 10405
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  |  |  | ROOM 10 C | 10672.5 | ROOM 10 C | 512.25
0.5um | 2015-05-04 | 1230000 | 1140000 | 1140000 | 1260000 | 1192500 | 61846.5844 | Pass | PEM |  |  | BREAK ROOM | 1125000 | BREAK ROOM | 2365
[particles/m^3]
5.0um | 2015-05-04 | 3250 | 3740 | 3180 | 2610 | 3195 | 462.7814 | Pass | PEM
[particles/m^3]
ROOM 21 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 21 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6 | Average | Standard | Pass/Fail | Initials
MAIN |  | [N wall] | [S wall] | [E wall] | [W wall] | [N Test] | [S test] |  | Dev | ISO 8
0.5um | 2015-04-28 | 863000 | 948000 | 1310000 | 985000 | 956000 | 801000 | 977166.6667 | 176752.2749 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-28 | 6220 | 2970 | 9680 | 6570 | 7270 | 3320 | 6005 | 2525.5395 | Pass | PEM
[particles/m^3]
ROOM 17 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 17 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-04-30 | 702000 | 659000 | 682000 | 869000 | 728000 | 95627.7505 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-30 | 9040 | 6430 | 9180 | 23800 | 12112.5 | 7893.6319 | Pass | PEM
[particles/m^3]
ROOM 15 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 15 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-04-28 | 56300 | 3880 | 47600 | 12400 | 30045 | 25777.615 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-28 | 2680 | 0 | 2970 | 848 | 1624.5 | 1433.6902 | Pass | PEM
[particles/m^3]
ROOM 14 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 14 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-04-30 | 652000 | 625000 | 695000 | 716000 | 672000 | 41125.8232 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-30 | 3390 | 1550 | 3250 | 2750 | 2735 | 836.401 | Pass | PEM
[particles/m^3]
ROOM 12 INNER CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 12 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6 | Average | Standard | Pass/Fail | Initials
INNER |  | [N wall] | [N wall] | [S wall] | [S wall] | [Mid pt] | [Mid Pt] |  | Dev | ISO 8
0.5um | 2015-05-05 | 5720 | 3110 | 29900 | 23000 | 1620 | 1200 | 10758.3333 | 12450.0159 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-05 | 283 | 212 | 3110 | 2050 | 212 | 0 | 977.8333 | 1289.0018 | Pass | PEM
[particles/m^3]
ROOM 12 OUTER CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 12 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
OUTER |  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-05-05 | 16100 | 10800 | 33200 | 32000 | 23025 | 11276.6351 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-05 | 2050 | 848 | 2680 | 2190 | 1942 | 777.742 | Pass | PEM
[particles/m^3]
ROOM 10 GOWNING ROOM PARTICLE TRACKING SHEET
ROOM 10 | Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials
GOWNING RM |  | [N wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-05-04 | 451000 | 462000 | 456500 | 7778.1746 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-04 | 11700 | 9110 | 10405 | 1831.4066 | Pass | PEM
[particles/m^3]
ROOM 10 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 10 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
CLEANROOM |  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-05-04 | 14800 | 2190 | 18500 | 7200 | 10672.5 | 7355.6571 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-04 | 848 | 0 | 918 | 283 | 512.25 | 444.341 | Pass | PEM
[particles/m^3]
Break Room CLEAN ROOM PARTICLE TRACKING SHEET
| Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials
BREAK ROOM |  | [N wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-04-28 | 1070000 | 1180000 | 1125000 | 77781.7459 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-28 | 2120 | 2610 | 2365 | 346.4823 | Pass | PEM
[particles/m^3]