## June 9th
ISO 8 Pass / Fail
ROOM 21B CLEAN ROOM PARTICLE TRACKING SHEET | [9 empty] | 0.5 um | 5.0 um | ROOM | AVE | 2015-06-09 | ROOM | AVE
[10 empty] | 3500000 | 29000 |  | 0.5um | File# |  | 5.0um
ROOM 21 B | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials |  |  |  | [particles/m^3] |  |  | [particles/m^3]
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  |  |  | ROOM 21 B | 2306666.6667 | 127-130 | ROOM 21 B | 1765
0.5um | 2015-06-09 | 2690000 | 2.34+06 | 2160000 | 2070000 | 2306666.6667 | 335012.4376 | Pass | PEM |  |  | ROOM 21 A | 39766.6667 | 131-134 | ROOM 21 A | 457.25
[particles/m^3] | File | 127 | 128 | 129 | 130 | [6 empty] | ROOM 21 | 1244500 | 135-138 | ROOM 21 | 9508.5
5.0um | 2015-06-09 | 1770 | 1340 | 2610 | 1340 | 1765 | 598.693 | Pass | PEM |  |  | ROOM 17 | 216000 | 139-142 | ROOM 17 | 7470
[particles/m^3] | [11 empty] | ROOM 15 | 676000 | 143-146 | ROOM 15 | 936
[12 empty] | ROOM 14 | 273000 | 147-150 | ROOM 14 | 937
ROOM 21A CLEAN ROOM PARTICLE TRACKING SHEET | [11 empty] | ROOM 12 I | 17500 | 151-154 | ROOM 12 I | 1270
[12 empty] | ROOM 12 O | 16800 | 155-156 | ROOM 12 O | 1490
ROOM 21 A | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials |  |  | ROOM 10 G | N/A |  | ROOM 10 G | N/A
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  |  |  | ROOM 10 C | N/A |  | ROOM 10 C | N/A
0.5um | 2015-06-09 | 7.14E+E04 | 37700 | 39100 | 42500 | 39766.6667 | 2468.4678 | Pass | PEM |  |  | BREAK ROOM | N/A |  | BREAK ROOM | N/A
[particles/m^3] | File | 131 | 132 | 133
5.0um | 2015-06-09 | 141 | 134 | 424 | 1130 | 457.25 | 468.4025 | Pass | PEM |  | Cleaning prior to scans reveals higher particle counts when compared to previous measurements in April May data.
[particles/m^3]
ROOM 21 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 21 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
MAIN |  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 1770000 | 1470000 | 1270000 | 468000 | 1244500 | 556956.9104 | Pass | PEM
[particles/m^3] | File | 135 | 136 | 137 | 138
5.0um | 2015-06-09 | 5510 | 23700 | 8330 | 494 | 9508.5 | 10000.6124 | Pass | PEM
[particles/m^3]
ROOM 17 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 17 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 424000 | 392000 | 36700 | 9460 | 215540 | 222894.9044 | Pass | PEM
[particles/m^3] | File | 139 | 140 | 141 | 142
5.0um | 2015-06-09 | 1550 | 2540 | 1980 | 23800 | 7467.5 | 10895.875 | Pass | PEM
[particles/m^3]
ROOM 15 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 15 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 18100 | 6360 | 1660000 | 1020000 | 676115 | 809905.7737 | Pass | PEM
[particles/m^3] | File | 143 | 144 | 145 | 146
5.0um | 2015-06-09 | 1200 | 353 | 1130 | 1060 | 935.75 | 392.6817 | Pass | PEM
[particles/m^3]
ROOM 14 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 539000 | 535000 | 6570 | 12700 | 273317.5 | 304488.9881 | Pass | PEM
[particles/m^3] | File | 147 | 148 | 149 | 150
5.0um | 2015-06-09 | 706 | 636 | 565 | 1840 | 936.75 | 604.9118 | Pass | PEM
[particles/m^3]
ROOM 12 INNER CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 12 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
INNER |  | [N wall] | [N wall] | [S wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 6070 | 3740 | 32300 | 27800 | 17477.5 | 14664.134 | Pass | PEM
[particles/m^3] | File | 151 | 152 | 153 | 154
5.0um | 2015-06-09 | 565 | 283 | 1770 | 2470 | 1272 | 1026.5116 | Pass | PEM
[particles/m^3]
ROOM 12 OUTER CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 12 | Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials
OUTER |  | [N wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 18100 | 15400 | 16750 | 1909.1883 | Pass | PEM
[particles/m^3] |  | 155 | 156
5.0um | 2015-06-09 | 1770 | 1200 | 1485 | 403.0509 | Pass | PEM
[particles/m^3]
ROOM 10 GOWNING ROOM PARTICLE TRACKING SHEET
ROOM 10 | Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials
GOWNING RM |  | [N wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 451000 | 462000 | 456500 | 7778.1746 | Pass | PEM
[particles/m^3]
5.0um | 2015-06-09 | 11700 | 9110 | 10405 | 1831.4066 | Pass | PEM
[particles/m^3]
ROOM 10 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 10 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
CLEANROOM |  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 14800 | 2190 | 18500 | 7200 | 10672.5 | 7355.6571 | Pass | PEM
[particles/m^3]
5.0um | 2015-06-09 | 848 | 0 | 918 | 283 | 512.25 | 444.341 | Pass | PEM
[particles/m^3]
Break Room CLEAN ROOM PARTICLE TRACKING SHEET
| Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials
BREAK ROOM |  | [N wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-06-09 | 1070000 | 1180000 | 1125000 | 77781.7459 | Pass | PEM
[particles/m^3]
5.0um | 2015-06-09 | 2120 | 2610 | 2365 | 346.4823 | Pass | PEM
[particles/m^3]

## April 28th-May 5th
ROOM 21B CLEAN ROOM PARTICLE TRACKING SHEET | [11 empty] | ROOM | AVE | ROOM | AVE
[13 empty] | 0.5um |  | 5.0um
ROOM 21 B | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials |  |  |  | [particles/m^3] |  | [particles/m^3]
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  |  |  | ROOM 21 B | 14285 | ROOM 21 B | 689.75
0.5um | 2015-05-01 | 15100 | 4240 | 12800 | 25000 | 14285 | 8535.8597 | Pass | PEM |  |  | ROOM 21 A | 1192500 | ROOM 21 A | 3195
[particles/m^3] | [11 empty] | ROOM 21 | 977166.6667 | ROOM 21 | 6005
5.0um | 2015-05-01 | 565 | 141 | 353 | 1700 | 689.75 | 695.3883 | Pass | PEM |  |  | ROOM 17 | 728000 | ROOM 17 | 12112.5
[particles/m^3] | [11 empty] | ROOM 15 | 30045 | ROOM 15 | 1624.5
[12 empty] | ROOM 14 | 672000 | ROOM 14 | 2735
ROOM 21A CLEAN ROOM PARTICLE TRACKING SHEET | [11 empty] | ROOM 12 I | 10758.3333 | ROOM 12 I | 977.8333
[12 empty] | ROOM 12 O | 23025 | ROOM 12 O | 1942
ROOM 21 A | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials |  |  | ROOM 10 G | 456500 | ROOM 10 G | 10405
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  |  |  | ROOM 10 C | 10672.5 | ROOM 10 C | 512.25
0.5um | 2015-05-04 | 1230000 | 1140000 | 1140000 | 1260000 | 1192500 | 61846.5844 | Pass | PEM |  |  | BREAK ROOM | 1125000 | BREAK ROOM | 2365
[particles/m^3]
5.0um | 2015-05-04 | 3250 | 3740 | 3180 | 2610 | 3195 | 462.7814 | Pass | PEM
[particles/m^3]
ROOM 21 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 21 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6 | Average | Standard | Pass/Fail | Initials
MAIN |  | [N wall] | [S wall] | [E wall] | [W wall] | [N Test] | [S test] |  | Dev | ISO 8
0.5um | 2015-04-28 | 863000 | 948000 | 1310000 | 985000 | 956000 | 801000 | 977166.6667 | 176752.2749 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-28 | 6220 | 2970 | 9680 | 6570 | 7270 | 3320 | 6005 | 2525.5395 | Pass | PEM
[particles/m^3]
ROOM 17 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 17 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-04-30 | 702000 | 659000 | 682000 | 869000 | 728000 | 95627.7505 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-30 | 9040 | 6430 | 9180 | 23800 | 12112.5 | 7893.6319 | Pass | PEM
[particles/m^3]
ROOM 15 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 15 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-04-28 | 56300 | 3880 | 47600 | 12400 | 30045 | 25777.615 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-28 | 2680 | 0 | 2970 | 848 | 1624.5 | 1433.6902 | Pass | PEM
[particles/m^3]
ROOM 14 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 14 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-04-30 | 652000 | 625000 | 695000 | 716000 | 672000 | 41125.8232 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-30 | 3390 | 1550 | 3250 | 2750 | 2735 | 836.401 | Pass | PEM
[particles/m^3]
ROOM 12 INNER CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 12 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6 | Average | Standard | Pass/Fail | Initials
INNER |  | [N wall] | [N wall] | [S wall] | [S wall] | [Mid pt] | [Mid Pt] |  | Dev | ISO 8
0.5um | 2015-05-05 | 5720 | 3110 | 29900 | 23000 | 1620 | 1200 | 10758.3333 | 12450.0159 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-05 | 283 | 212 | 3110 | 2050 | 212 | 0 | 977.8333 | 1289.0018 | Pass | PEM
[particles/m^3]
ROOM 12 OUTER CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 12 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
OUTER |  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-05-05 | 16100 | 10800 | 33200 | 32000 | 23025 | 11276.6351 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-05 | 2050 | 848 | 2680 | 2190 | 1942 | 777.742 | Pass | PEM
[particles/m^3]
ROOM 10 GOWNING ROOM PARTICLE TRACKING SHEET
ROOM 10 | Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials
GOWNING RM |  | [N wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-05-04 | 451000 | 462000 | 456500 | 7778.1746 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-04 | 11700 | 9110 | 10405 | 1831.4066 | Pass | PEM
[particles/m^3]
ROOM 10 CLEAN ROOM PARTICLE TRACKING SHEET
ROOM 10 | Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials
CLEANROOM |  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8
0.5um | 2015-05-04 | 14800 | 2190 | 18500 | 7200 | 10672.5 | 7355.6571 | Pass | PEM
[particles/m^3]
5.0um | 2015-05-04 | 848 | 0 | 918 | 283 | 512.25 | 444.341 | Pass | PEM
[particles/m^3]
Break Room CLEAN ROOM PARTICLE TRACKING SHEET
| Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials
BREAK ROOM |  | [N wall] | [S wall] |  | Dev | ISO 8
0.5um | 2015-04-28 | 1070000 | 1180000 | 1125000 | 77781.7459 | Pass | PEM
[particles/m^3]
5.0um | 2015-04-28 | 2120 | 2610 | 2365 | 346.4823 | Pass | PEM
[particles/m^3]

## Comparison 1st scan to 2nd
ROOM | AVE | April-May | ROOM | AVE
| 0.5um |  |  | 5.0um
| [particles/m^3] |  |  | [particles/m^3]
ROOM 21 B | 14285 | April-May | ROOM 21 B | 689.75
ROOM 21 A | 1192500 | April-May | ROOM 21 A | 3195
ROOM 21 | 977166.6667 | April-May | ROOM 21 | 6005
ROOM 17 | 728000 | April-May | ROOM 17 | 12112.5
ROOM 15 | 30045 | April-May | ROOM 15 | 1624.5
ROOM 14 | 672000 | April-May | ROOM 14 | 2735
ROOM 12 I | 10758.3333 | April-May | ROOM 12 I | 977.8333
ROOM 12 O | 23025 | April-May | ROOM 12 O | 1942
ROOM 10 G | 456500 | April-May | ROOM 10 G | 10405
ROOM 10 C | 10672.5 | April-May | ROOM 10 C | 512.25
BREAK ROOM | 1125000 | April-May | BREAK ROOM | 2365
ROOM | AVE | June 9th | ROOM | AVE
| 0.5um | File# |  | 5.0um
| [particles/m^3] |  |  | [particles/m^3]
ROOM 21 B | 2306666.6667 | June 9th | ROOM 21 B | 1765
ROOM 21 A | 39766.6667 | June 9th | ROOM 21 A | 457.25
ROOM 21 | 1244500 | June 9th | ROOM 21 | 9508.5
ROOM 17 | 216000 | June 9th | ROOM 17 | 7470
ROOM 15 | 676000 | June 9th | ROOM 15 | 936
ROOM 14 | 273000 | June 9th | ROOM 14 | 937
ROOM 12 I | 17500 | June 9th | ROOM 12 I | 1270
ROOM 12 O | 16800 | June 9th | ROOM 12 O | 1490
ROOM 10 G | N/A |  | ROOM 10 G | N/A
ROOM 10 C | N/A |  | ROOM 10 C | N/A
BREAK ROOM | N/A |  | BREAK ROOM | N/A
ROOM | AVE | Delta | ROOM | AVE
| 0.5um |  |  | 5.0um
| [particles/m^3] |  |  | [particles/m^3]
ROOM 21 B | 2292381.6667 |  | ROOM 21 B | 1075.25
ROOM 21 A | -1152733.3333 |  | ROOM 21 A | -2737.75
ROOM 21 | 267333.3333 |  | ROOM 21 | 3503.5
ROOM 17 | 216000 |  | ROOM 17 | 7470
ROOM 15 | 676000 |  | ROOM 15 | 936
ROOM 14 | 273000 |  | ROOM 14 | 937
ROOM 12 I | 17500 |  | ROOM 12 I | 1270
ROOM 12 O | 16800 |  | ROOM 12 O | 1490
ROOM 10 G | N/A |  | ROOM 10 G | N/A
ROOM 10 C | N/A |  | ROOM 10 C | N/A
BREAK ROOM | N/A |  | BREAK ROOM | N/A
ROOM May and June | May AVE | June AVE | ROOM May and June | May AVE | June AVE
| 0.5um | 0.5um |  | 5.0um | 5.0um
| [particles/m^3] | [particles/m^3] |  | [particles/m^3] | [particles/m^3]
ROOM 21 B | 14285 | 2306666.6667 | ROOM 21 B | 689.75 | 1765
ROOM 21 A | 1192500 | 39766.6667 | ROOM 21 A | 3195 | 457.25
ROOM 21 | 977166.6667 | 1244500 | ROOM 21 | 6005 | 9508.5
ROOM 17 | 728000 | 216000 | ROOM 17 | 12112.5 | 7470
ROOM 15 | 30045 | 676000 | ROOM 15 | 1624.5 | 936
ROOM 14 | 672000 | 273000 | ROOM 14 | 2735 | 937
ROOM 12 I | 10758.3333 | 17500 | ROOM 12 I | 977.8333 | 1270
ROOM 12 O | 23025 | 16800 | ROOM 12 O | 1942 | 1490