## Room 21B A=231.25 sq ft
ROOM 21B CLEAN ROOM PARTICLE TRACKING SHEET
Handheld LPC Data Retrieval Software
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials | Mode: ISO
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  | Start Time:2015-04-30 11:13:21
0.5um | 2015-05-01 | 15100 | 4240 | 12800 | 25000 | 14285 | 8535.8597 | Pass | PEM | Stop Time:2015-04-30 11:55:51
[particles/m^3]
5.0um | 2015-05-01 | 565 | 141 | 353 | 1700 | 689.75 | 695.3883 | Pass | PEM | Point1
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 85B
0.5um | [9 empty] | 2015-04-30 11:13 | 1 | 283 | 0 | /m3
[particles/m^3] | [10 empty] | AVG | 283 | 0 | /m3
5.0um | [9 empty] | Point2
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21B | File 86B
0.5um | [9 empty] | 2015-04-30 11:27 | 1 | 15100 | 565 | /m3 | Midpoint Length Left
[particles/m^3] | [10 empty] | AVG | 15100 | 565 | /m3
5.0um | [9 empty] | Point3
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 87B
0.5um | [9 empty] | 2015-04-30 11:35 | 1 | 4240 | 141 | /m3 | Midpoint Length Right
[particles/m^3] | [10 empty] | AVG | 4240 | 141 | /m3
5.0um | [9 empty] | Point4
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 88B
0.5um | [9 empty] | 2015-04-30 11:41 | 1 | 12800 | 353 | /m3 | Midpoint Width Back
[particles/m^3] | [10 empty] | AVG | 12800 | 353 | /m3
5.0um | [9 empty] | Point5
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 89B
0.5um | [9 empty] | 2015-04-30 11:56 | 1 | 25000 | 1700 | /m3 | Midpoint Width Front
[particles/m^3] | [10 empty] | AVG | 25000 | 1700 | /m3
5.0um | [9 empty] | Pure Class
[particles/m^3] | [10 empty] | AVG | SD | 95%UCL | Unit
0.5um | [9 empty] | 0.5um | 11500 | 9680 | 20600 | /m3
[particles/m^3] | [9 empty] | 5.0um | 551 | 675 | 1180 | /m3
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um | [9 empty] | ****Time was set incorrectly, but corrected after the test.**** Need to set time before running scans in the future! All scans were 5 minutes in duration.
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
RM 21B 12.5 ft Wide x 18.5 ft Long
Area = 231.25 sq ft
231.25 square foot = 21.48 square meter
Nl =SQRT of Area=15.2 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Room 21A A=231.25 sq ft
ROOM 21A CLEAN ROOM PARTICLE TRACKING SHEET
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials | Point1
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  | Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 94B
0.5um | 2015-05-04 | 1230000 | 1140000 | 1140000 | 1260000 | 1192500 | 61846.5844 | Pass | PEM | 2015-05-01 16:56 | 1 | 989 | 0 | /m3
[particles/m^3] | [10 empty] | AVG | 989 | 0 | /m3
5.0um | 2015-05-04 | 3250 | 3740 | 3180 | 2610 | 3195 | 462.7814 | Pass | PEM | Point2
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 95B
0.5um | [9 empty] | 2015-05-01 17:02 | 1 | 1230000 | 3250 | /m3 | Midpoint Length Left
[particles/m^3] | [10 empty] | AVG | 1230000 | 3250 | /m3
5.0um | [9 empty] | Pure Class
[particles/m^3] | [10 empty] | AVG | SD | 95%UCL | Unit | Room 21 | File
0.5um | [9 empty] | 0.5um | 1840 | 1300 | 7620 | /m3 | Midpoint Length Right
[particles/m^3] | [9 empty] | 5.0um | 318 | 250 | 1430 | /m3
5.0um | [9 empty] | Point1
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 96B
0.5um | [9 empty] | 2015-05-01 17:08 | 1 | 1140000 | 3740 | /m3 | Midpoint Width Left
[particles/m^3] | [10 empty] | AVG | 1140000 | 3740 | /m3
5.0um | [9 empty] | Point2
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 97B
0.5um | [9 empty] | 2015-05-01 17:13 | 1 | 1140000 | 3180 | /m3 | Midpoint Width Right
[particles/m^3] | [10 empty] | AVG | 1140000 | 3180 | /m3
5.0um | [9 empty] | Pure Class
[particles/m^3] | [10 empty] | AVG | SD | 95%UCL | Unit | Room 21 | File
0.5um | [9 empty] | 0.5um | 1840 | 1300 | 7620 | /m3 | Midpoint Length Left
[particles/m^3] | [9 empty] | 5.0um | 318 | 250 | 1430 | /m3
5.0um | [9 empty] | Point1
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 98B
0.5um | [9 empty] | 2015-05-01 17:19 | 1 | 1260000 | 2610 | /m3 | Midpoint Length Right
[particles/m^3] | [10 empty] | AVG | 1260000 | 2610 | /m3
5.0um
[particles/m^3]
0.5um
[particles/m^3] | [9 empty] | ****Time was set incorrectly, but corrected after the test.**** Need to set time before running scans in the future! All scans were 5 minutes in duration.
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
RM 21B 12.5 ft Wide x 18.5 ft Long
Area = 231.25 sq ft
231.25 square foot = 21.48 square meter
Nl =SQRT of Area=15.2 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Room 21 A=1440 sq ft
ROOM 21 CLEAN ROOM PARTICLE TRACKING SHEET
Point1
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 62B
|  | [N wall] | [S wall] | [E wall] | [W wall] | [N Test] | [S test] |  | Dev | ISO 8 |  | 2015-04-28 20:42 | 1 | 0 | 0 | /m3
0.5um | 2015-04-28 | 863000 | 948000 | 1310000 | 985000 | 956000 | 801000 | 977166.6667 | 176752.2749 | Pass | PEM |  | AVG | 0 | 0 | /m3
[particles/m^3] | [11 empty] | Point2
5.0um | 2015-04-28 | 6220 | 2970 | 9680 | 6570 | 7270 | 3320 | 6005 | 2525.5395 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 63B
[particles/m^3] | [11 empty] | 2015-04-28 21:07 | 1 | 863000 | 6220 | /m3 | Midpoint Length Left
0.5um | [12 empty] | AVG | 863000 | 6220 | /m3
[particles/m^3] | [11 empty] | Point3
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 64B
[particles/m^3] | [11 empty] | 2015-04-28 21:13 | 1 | 948000 | 2970 | /m3 | Midpoint Length Right
0.5um | [12 empty] | AVG | 948000 | 2970 | /m3
[particles/m^3] | [11 empty] | Point4
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 65B
[particles/m^3] | [11 empty] | 2015-04-28 21:19 | 1 | 1310000 | 9680 | /m3 | Midpoint Width Left
0.5um | [12 empty] | AVG | 1310000 | 9680 | /m3
[particles/m^3] | [11 empty] | Point5
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 66B
[particles/m^3] | [11 empty] | 2015-04-28 21:25 | 1 | 985000 | 6570 | /m3 | Midpoint Width Right
0.5um | [12 empty] | AVG | 985000 | 6570 | /m3
[particles/m^3] | [11 empty] | Point6
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 67B
[particles/m^3] | [11 empty] | 2015-04-28 21:31 | 1 | 956000 | 7270 | /m3 | Midpoint Length Left
0.5um | [12 empty] | AVG | 956000 | 7270 | /m3
[particles/m^3] | [11 empty] | Point7
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 68B
[particles/m^3] | [11 empty] | 2015-04-28 23:26 | 1 | 801000 | 3320 | /m3 | Midpoint Length Right
0.5um | [12 empty] | AVG | 801000 | 3320 | /m3
[particles/m^3]
5.0um | [11 empty] | ****Time was set incorrectly, but corrected after the test.**** All scans were 5 minutes in duration.
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
RM 21 30 ft Wide x 48 ft Long
Area = 1440 sq ft
1 440 square foot = 133.78 square meter
Nl =SQRT of Area=37.9 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Room 17 A= 388.5 sq ft
ROOM 17 CLEAN ROOM PARTICLE TRACKING SHEET
Point1
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 76B
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  | 2015-04-30 05:13 | 1 | 636 | 0 | /m3 | Zero Filter Test
0.5um | 2015-04-30 | 702000 | 659000 | 682000 | 869000 | 728000 | 95627.7505 | Pass | PEM |  | AVG | 636 | 0 | /m3
[particles/m^3] | [9 empty] | Point2
5.0um | 2015-04-30 | 9040 | 6430 | 9180 | 23800 | 12112.5 | 7893.6319 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 77B
[particles/m^3] | [9 empty] | 2015-04-30 05:19 | 1 | 702000 | 9040 | /m3 | Right Side Front
0.5um | [10 empty] | AVG | 702000 | 9040 | /m3
[particles/m^3] | [9 empty] | Point3
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 78B
[particles/m^3] | [9 empty] | 2015-04-30 05:25 | 1 | 659000 | 6430 | /m3 | Left Side Rear
0.5um | [10 empty] | AVG | 659000 | 6430 | /m3
[particles/m^3] | [9 empty] | Point4
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 79B
[particles/m^3] | [9 empty] | 2015-04-30 05:31 | 1 | 682000 | 9180 | /m3 | Right Side Middle
0.5um | [10 empty] | AVG | 682000 | 9180 | /m3
[particles/m^3] | [9 empty] | Point5
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 80B
[particles/m^3] | [9 empty] | 2015-04-30 05:36 | 1 | 869000 | 23800 | /m3 | Left Side Middle
0.5um | [10 empty] | AVG | 869000 | 23800 | /m3
[particles/m^3]
5.0um
[particles/m^3]
0.5um | [9 empty] | ****Time was set incorrectly, but corrected after the test.**** All scans were 5 minutes in duration.
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
RM 17 18.5 ft Wide x 21 ft Long
Area = 388.5 sq ft
388.5 square foot = 36.092 square meter
Nl =SQRT of Area=19.7 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Room 15 A=653.25 sq ft
ROOM 15 CLEAN ROOM PARTICLE TRACKING SHEET
Point11
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 72B
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  | 2015-04-28 23:56 | 1 | 56300 | 2680 | /m3 | Left Side Rear
0.5um | 2015-04-28 | 56300 | 3880 | 47600 | 12400 | 30045 | 25777.615 | Pass | PEM |  | AVG | 56300 | 2680 | /m3
[particles/m^3] | [9 empty] | Point12
5.0um | 2015-04-28 | 2680 | 0 | 2970 | 848 | 1624.5 | 1433.6902 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 73B
[particles/m^3] | [9 empty] | 2015-04-29 00:07 | 1 | 3880 | 0 | /m3 | Left Side Front
0.5um | [10 empty] | AVG | 3880 | 0 | /m3
[particles/m^3] | [9 empty] | Point13
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 74B
[particles/m^3] | [9 empty] | 2015-04-29 00:17 | 1 | 47600 | 2970 | /m3 | Right Side Rear
0.5um | [10 empty] | AVG | 47600 | 2970 | /m3
[particles/m^3] | [9 empty] | Point14
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 75B
[particles/m^3] | [9 empty] | 2015-04-29 00:32 | 1 | 12400 | 848 | /m3 | Right Side Front
0.5um | [10 empty] | AVG | 12400 | 848 | /m3
[particles/m^3]
5.0um
[particles/m^3]
0.5um | [9 empty] | ****Time was set incorrectly, but corrected after the test.**** All scans were 5 minutes in duration.
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
RM 15 19.5 ft Wide x 33.5 ft Long
Area = 653.25 sq ft
653.25 square foot = 60.688 square meter
Nl =SQRT of Area=25.5 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Room 14 Cleaning Area
ROOM 14 CLEAN ROOM PARTICLE TRACKING SHEET
Point6
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 81B
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  | 2015-04-30 05:46 | 1 | 652000 | 3390 | /m3 | Left Side Middle
0.5um | 2015-04-30 | 652000 | 625000 | 695000 | 716000 | 672000 | 41125.8232 | Pass | PEM |  | AVG | 652000 | 3390 | /m3
[particles/m^3] | [9 empty] | Point7
5.0um | 2015-04-30 | 3390 | 1550 | 3250 | 2750 | 2735 | 836.401 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 82B
[particles/m^3] | [9 empty] | 2015-04-30 05:56 | 1 | 625000 | 1550 | /m3 | Right Side near Ultrasonic Tank
0.5um | [10 empty] | AVG | 625000 | 1550 | /m3
[particles/m^3] | [9 empty] | Point8
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 83B
[particles/m^3] | [9 empty] | 2015-04-30 06:03 | 1 | 695000 | 3250 | /m3 | Right Side Rear
0.5um | [10 empty] | AVG | 695000 | 3250 | /m3
[particles/m^3] | [9 empty] | Point9
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 84B
[particles/m^3] | [9 empty] | 2015-04-30 06:13 | 1 | 716000 | 2750 | /m3 | Right Side Front
0.5um | [10 empty] | AVG | 716000 | 2750 | /m3
[particles/m^3]
5.0um
[particles/m^3]
0.5um | [9 empty] | ****Time was set incorrectly, but corrected after the test.**** All scans were 5 minutes in duration.
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
Room 10 X ft Wide x Y ft Long
Area = XY sq ft
square foot = square meter
Nl =SQRT of Area= locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Room 12 Inner
ROOM 12 CLEAN ROOM PARTICLE TRACKING SHEET
[12 empty] | Point6 | [8 empty] | Point6
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Zone 5 | Zone 6 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 |  |  | File 104B | Date & time | Times | 0.5um | 5.0um | Unit
|  | [N wall] | [N wall] | [S wall] | [S wall] | [Mid pt] | [Mid Pt] |  | Dev | ISO 8 |  | 2015-05-05 09:49 | 1 | 5720 | 283 | /m3 | North Wall |  |  |  | 2015-05-05 09:49 | 1 | 5720 | 283 | /m3
0.5um | 2015-05-05 | 5720 | 3110 | 29900 | 23000 | 1620 | 1200 | 10758.3333 | 12450.0159 | Pass | PEM |  | AVG | 5720 | 283 | /m3 | [5 empty] | AVG | 5720 | 283 | /m3
[particles/m^3] | [11 empty] | Point1 | [8 empty] | Pure Class
5.0um | 2015-05-05 | 283 | 212 | 3110 | 2050 | 212 | 0 | 977.8333 | 1289.0018 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 |  |  | File 105B |  | AVG | SD | 95%UCL | Unit
[particles/m^3] | [11 empty] | 2015-05-05 09:55 | 1 | 3110 | 212 | /m3 | North Wall |  |  |  | 0.5um | 5910 | 5460 | 10400 | /m3
0.5um | [12 empty] | AVG | 3110 | 212 | /m3 |  |  |  |  | 5.0um | 988 | 1150 | 1920 | /m3
[particles/m^3] | [11 empty] | Point2
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 |  |  | File 106B | Point1
[particles/m^3] | [11 empty] | 2015-05-05 10:02 | 1 | 29900 | 3110 | /m3 | South Wall |  |  |  | Date & time | Times | 0.5um | 5.0um | Unit
0.5um | [12 empty] | AVG | 29900 | 3110 | /m3 |  |  |  |  | 2015-05-05 09:55 | 1 | 3110 | 212 | /m3
[particles/m^3] | [11 empty] | Point3 | [9 empty] | AVG | 3110 | 212 | /m3
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 |  |  | File 107B | Point2
[particles/m^3] | [11 empty] | 2015-05-05 10:08 | 1 | 23000 | 2050 | /m3 | South Wall |  |  |  | Date & time | Times | 0.5um | 5.0um | Unit
0.5um | [12 empty] | AVG | 23000 | 2050 | /m3 |  |  |  |  | 2015-05-05 10:02 | 1 | 29900 | 3110 | /m3
[particles/m^3] | [11 empty] | Point4 | [9 empty] | AVG | 29900 | 3110 | /m3
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 |  |  | File 108B | Point3
[particles/m^3] | [11 empty] | 2015-05-05 10:14 | 1 | 1620 | 212 | /m3 | Middle of Lab |  |  |  | Date & time | Times | 0.5um | 5.0um | Unit
0.5um | [12 empty] | AVG | 1620 | 212 | /m3 |  |  |  |  | 2015-05-05 10:08 | 1 | 23000 | 2050 | /m3
[particles/m^3] | [11 empty] | Point5 | [9 empty] | AVG | 23000 | 2050 | /m3
5.0um | [11 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 |  |  | File 109B | Point4
[particles/m^3] | [11 empty] | 2015-05-05 10:19 | 1 | 1200 | 0 | /m3 | Middle of Lab |  |  |  | Date & time | Times | 0.5um | 5.0um | Unit
0.5um | [12 empty] | AVG | 1200 | 0 | /m3 |  |  |  |  | 2015-05-05 10:14 | 1 | 1620 | 212 | /m3
[particles/m^3] | [21 empty] | AVG | 1620 | 212 | /m3
5.0um | [20 empty] | Point5
[particles/m^3] | [20 empty] | Date & time | Times | 0.5um | 5.0um | Unit
0.5um | [20 empty] | 2015-05-05 10:19 | 1 | 1200 | 0 | /m3
[particles/m^3] | [21 empty] | AVG | 1200 | 0 | /m3
5.0um | [11 empty] | ****Time was set correctly.**** All scans were 5 minutes in duration. | [8 empty] | Pure Class
[particles/m^3] | [21 empty] | AVG | SD | 95%UCL | Unit
0.5um | [20 empty] | 0.5um | 5910 | 5460 | 10400 | /m3
[particles/m^3] | [20 empty] | 5.0um | 988 | 1150 | 1920 | /m3
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000) | [11 empty] | Class | maximum particles/m3 | [5 empty] | FED STD 209E
0.5um |  | 5.0um | [10 empty] | ≥0.1 µm | ≥0.2 µm | ≥0.3 µm | ≥0.5 µm | ≥1 µm | ≥5 µm | equivalent
3.52x10^6/m^3 |  | 2.93x10^4/m^3 | [9 empty] | ISO 6 | 1.0×106 | 237000 | 102000 | 35200 | 8320 | 293 | Class 1,000
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
Room 12 X 20ft Wide x 20 ft Long
Area = 400 sq ft
400 square foot = 37.161 square meter
Nl =SQRT of Area= 20 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.
We meet the callout for ISO 6 Class clean room per ISO 14644 for the 0.5 Micron particles and we don't meet the requirement for 5.0 micron size particles. To qualify the cleanroom we would need a better Particle Counter with more channels that monitor smaller particles.

## Room 12 Outer Area
ROOM 12 CLEAN ROOM PARTICLE TRACKING SHEET
[10 empty] | Point1 | [8 empty] | Point1
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 Outer |  |  | File 100B | Date & time | Times | 0.5um | 5.0um | Unit
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  | 2015-05-05 09:19 | 1 | 70.6 | 0 | /m3 | Zero Filter |  |  |  | 2015-05-05 09:19 | 1 | 70.6 | 0 | /m3
0.5um | 2015-05-05 | 16100 | 10800 | 33200 | 32000 | 23025 | 11276.6351 | Pass | PEM |  | AVG | 70.6 | 0 | /m3 | [5 empty] | AVG | 70.6 | 0 | /m3
[particles/m^3] | [9 empty] | Point2 | [8 empty] | Point2
5.0um | 2015-05-05 | 2050 | 848 | 2680 | 2190 | 1942 | 777.742 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 Outer |  |  | File 101B | Date & time | Times | 0.5um | 5.0um | Unit
[particles/m^3] | [9 empty] | 2015-05-05 09:25 | 1 | 16100 | 2050 | /m3 | North Wall |  |  |  | 2015-05-05 09:25 | 1 | 16100 | 2050 | /m3
0.5um | [10 empty] | AVG | 16100 | 2050 | /m3 | [5 empty] | AVG | 16100 | 2050 | /m3
[particles/m^3] | [9 empty] | Point3 | [8 empty] | Point3
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 Outer |  |  | File 102B | Date & time | Times | 0.5um | 5.0um | Unit
[particles/m^3] | [9 empty] | 2015-05-05 09:31 | 1 | 10800 | 848 | /m3 | North Wall |  |  |  | 2015-05-05 09:31 | 1 | 10800 | 848 | /m3
0.5um | [10 empty] | AVG | 10800 | 848 | /m3 | [5 empty] | AVG | 10800 | 848 | /m3
[particles/m^3] | [9 empty] | Point4 | [8 empty] | Point4
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 Outer |  |  | File 103B | Date & time | Times | 0.5um | 5.0um | Unit
[particles/m^3] | [9 empty] | 2015-05-05 09:37 | 1 | 33200 | 2680 | /m3 | South Wall |  |  |  | 2015-05-05 09:37 | 1 | 33200 | 2680 | /m3
0.5um | [10 empty] | AVG | 33200 | 2680 | /m3 | [5 empty] | AVG | 33200 | 2680 | /m3
[particles/m^3] | [9 empty] | Point5 | [8 empty] | Point5
5.0um | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 12 Outer |  |  | File 103B | Date & time | Times | 0.5um | 5.0um | Unit
[particles/m^3] | [9 empty] | 2015-05-05 09:43 | 1 | 32000 | 2190 | /m3 | South Wall |  |  |  | 2015-05-05 09:43 | 1 | 32000 | 2190 | /m3
0.5um | [10 empty] | AVG | 32000 | 2190 | /m3 | [5 empty] | AVG | 32000 | 2190 | /m3
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um | [9 empty] | ****Time was set correctly.**** All scans were 5 minutes in duration.
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000) | [9 empty] | Class | maximum particles/m3 | [5 empty] | FED STD 209E
0.5um |  | 5.0um | [8 empty] | ≥0.1 µm | ≥0.2 µm | ≥0.3 µm | ≥0.5 µm | ≥1 µm | ≥5 µm | equivalent
3.52x10^5/m^3 |  | 2.93x10^3/m^3 | [7 empty] | ISO 6 | 1.0×106 | 237000 | 102000 | 35200 | 8320 | 293 | Class 1,000
Room 12 20 ft Wide x 20 ft Long
Area = 400 sq ft
400 square foot = 37.161 square meter
Nl =SQRT of Area= 20 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.
We barely meet the callout for ISO 6 Class clean room per ISO 14644 for the 0.5 Micron particles and we don't meet the requirement for 5.0 micron size particles.

## Room 10 GOWNING AREA
ROOM 10 GOWNING ROOM PARTICLE TRACKING SHEET
Point1
| Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 99B
|  | [N wall] | [S wall] |  | Dev | ISO 8 |  | 2015-05-01 18:05 | 1 | 0 | 0 | /m3
0.5um | 2015-05-04 | 451000 | 462000 | 456500 | 7778.1746 | Pass | PEM |  | AVG | 0 | 0 | /m3
[particles/m^3] | [7 empty] | Point2
5.0um | 2015-05-04 | 11700 | 9110 | 10405 | 1831.4066 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Room 10 Gowning | File 100B
[particles/m^3] | [7 empty] | 2015-05-01 18:10 | 1 | 451000 | 11700 | /m3 | Midpoint Length Left
0.5um | [8 empty] | AVG | 451000 | 11700 | /m3
[particles/m^3] | [7 empty] | Pure Class
5.0um | [8 empty] | AVG | SD | 95%UCL | Unit | Room 10 Gowning | File
[particles/m^3] | [7 empty] | 0.5um | 1840 | 1300 | 7620 | /m3
0.5um | [7 empty] | 5.0um | 318 | 250 | 1430 | /m3
[particles/m^3] | [7 empty] | Point1
5.0um | [7 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 10 Gowning | File 101B
[particles/m^3] | [7 empty] | 2015-05-01 18:16 | 1 | 462000 | 9110 | /m3 | Midpoint Width Back
0.5um | [8 empty] | AVG | 462000 | 9110 | /m3
[particles/m^3] | [7 empty] | Pure Class
5.0um | [8 empty] | AVG | SD | 95%UCL | Unit
[particles/m^3] | [7 empty] | 0.5um | 1840 | 1300 | 7620 | /m3
0.5um | [7 empty] | 5.0um | 318 | 250 | 1430 | /m3
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3] | [7 empty] | ****Time was set incorrectly, but corrected after the test.**** Need to set time before running scans in the future! All scans were 5 minutes in duration.
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
Room 10 9.3 ft Wide x 7.6 ft Long
Area = 70.68 sq ft = 6.56 square meter
Nl =SQRT of Area= locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Room 10 Clean Room
ROOM 10 CLEAN ROOM PARTICLE TRACKING SHEET
| Date | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Average | Standard | Pass/Fail | Initials | Point2
|  | [N wall] | [S wall] | [E wall] | [W wall] |  | Dev | ISO 8 |  | Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 90B
0.5um | 2015-05-04 | 14800 | 2190 | 18500 | 7200 | 10672.5 | 7355.6571 | Pass | PEM | 2015-05-01 17:36 | 1 | 0 | 0 | /m3
[particles/m^3] | [10 empty] | AVG | 0 | 0 | /m3
5.0um | 2015-05-04 | 848 | 0 | 918 | 283 | 512.25 | 444.341 | Pass | PEM | Point1
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 10 | File 91B
0.5um | [9 empty] | 2015-05-01 17:42 | 1 | 14800 | 848 | /m3 | Midpoint
[particles/m^3] | [10 empty] | AVG | 14800 | 848 | /m3
5.0um | [9 empty] | Point2
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 10 | File 92B
0.5um | [9 empty] | 2015-05-01 17:47 | 1 | 2190 | 0 | /m3 | Midpoint under HEPA
[particles/m^3] | [10 empty] | AVG | 2190 | 0 | /m3
5.0um | [9 empty] | Point1
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 10 | File 93B
0.5um | [9 empty] | 2015-05-01 17:53 | 1 | 18500 | 918 | /m3 | Midpoint Width Back
[particles/m^3] | [10 empty] | AVG | 18500 | 918 | /m3
5.0um | [9 empty] | Point2
[particles/m^3] | [9 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Room 10 | File 94B
0.5um | [9 empty] | 2015-05-01 17:58 | 1 | 7200 | 283 | /m3 | Midpoint Width Back
[particles/m^3] | [10 empty] | AVG | 7200 | 283 | /m3
5.0um | [9 empty] | Pure Class
[particles/m^3] | [10 empty] | AVG | SD | 95%UCL | Unit | Room 10 | File 95B
0.5um | [9 empty] | 0.5um | 1840 | 1300 | 7620 | /m3
[particles/m^3] | [9 empty] | 5.0um | 318 | 250 | 1430 | /m3
5.0um
[particles/m^3]
0.5um | [9 empty] | ****Time was set incorrectly, but corrected after the test.**** Need to set time before running scans in the future! All scans were 5 minutes in duration.
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
Room 10 10 ft Wide x 10 ft Long
Area = 100 sq ft
100 square foot = 9.29 square meter
Nl =SQRT of Area= 10 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.

## Break Room A= 161.25 sq ft
Break Room CLEAN ROOM PARTICLE TRACKING SHEET
Point8
| Date | Zone 1 | Zone 2 | Average | Standard | Pass/Fail | Initials | Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 69B
|  | [N wall] | [S wall] |  | Dev | ISO 8 |  | 2015-04-28 23:37 | 1 | 212 | 0 | /m3 | Break Room 20
0.5um | 2015-04-28 | 1070000 | 1180000 | 1125000 | 77781.7459 | Pass | PEM |  | AVG | 212 | 0 | /m3 | Midpoint Width Left
[particles/m^3] | [7 empty] | Point9
5.0um | 2015-04-28 | 2120 | 2610 | 2365 | 346.4823 | Pass | PEM | Date & time | Times | 0.5um | 5.0um | Unit | Break Room 20 | File 70B
[particles/m^3] | [7 empty] | 2015-04-28 23:42 | 1 | 1070000 | 2120 | /m3 | Midpoint Width Left
0.5um | [8 empty] | AVG | 1070000 | 2120 | /m3
[particles/m^3] | [7 empty] | Point10
5.0um | [7 empty] | Date & time | Times | 0.5um | 5.0um | Unit | Break Room 20 | File 71B
[particles/m^3] | [7 empty] | 2015-04-28 23:48 | 1 | 1180000 | 2610 | /m3 | End of Length Back
0.5um | [8 empty] | AVG | 1180000 | 2610 | /m3
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
0.5um
[particles/m^3]
5.0um | [7 empty] | ****Time was set incorrectly, but corrected after the test.**** All scans were 5 minutes in duration.
[particles/m^3]
0.5um
[particles/m^3]
5.0um
[particles/m^3]
ISO 8 Standard (i.e. Class 100,000)
0.5um |  | 5.0um
3.52x10^6/m^3 |  | 2.93x10^4/m^3
ISO 7 Standard (i.e. Class 10,000)
0.5um |  | 5.0um
3.52x10^5/m^3 |  | 2.93x10^3/m^3
Break Room 7.5 ft Wide x 21.5 ft Long
Area = 161.25 sq ft
161.25 square foot = 14.980 square meter
Nl =SQRT of Area=12.69 locations
Minimum Locations per FS 209E are 5 QTY
Minimum Locations per ISO 14644-1 are 3 QTY
Hector uses 6 locations during sampling see Excel file.
Due to the small size of the break room only two locations were recorded for the baseline readings.

## Raw Data
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 20:42 | 1 | 0 | 0 | /m3
| AVG | 0 | 0 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:07 | 1 | 863000 | 6220 | /m3
| AVG | 863000 | 6220 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:13 | 1 | 948000 | 2970 | /m3
| AVG | 948000 | 2970 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:19 | 1 | 1310000 | 9680 | /m3
| AVG | 1310000 | 9680 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:25 | 1 | 985000 | 6570 | /m3
| AVG | 985000 | 6570 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:31 | 1 | 956000 | 7270 | /m3
| AVG | 956000 | 7270 | /m3
Point7
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:26 | 1 | 801000 | 3320 | /m3
| AVG | 801000 | 3320 | /m3
Point8
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:37 | 1 | 212 | 0 | /m3
| AVG | 212 | 0 | /m3
Point9
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:42 | 1 | 1070000 | 2120 | /m3
| AVG | 1070000 | 2120 | /m3
Point10
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:48 | 1 | 1180000 | 2610 | /m3
| AVG | 1180000 | 2610 | /m3
Point11
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:56 | 1 | 56300 | 2680 | /m3
| AVG | 56300 | 2680 | /m3
Point12
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-29 00:07 | 1 | 3880 | 0 | /m3
| AVG | 3880 | 0 | /m3
Point13
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-29 00:17 | 1 | 47600 | 2970 | /m3
| AVG | 47600 | 2970 | /m3
Point14
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-29 00:32 | 1 | 12400 | 848 | /m3
| AVG | 12400 | 848 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 588000 | 524000 | ---- | /m3
5.0um | 3370 | 2990 | ---- | /m3

## Data 04 28 2015
Point1
Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 62B
2015-04-28 20:42 | 1 | 0 | 0 | /m3
| AVG | 0 | 0 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 63B
2015-04-28 21:07 | 1 | 863000 | 6220 | /m3 | Midpoint Length Left
| AVG | 863000 | 6220 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 64B
2015-04-28 21:13 | 1 | 948000 | 2970 | /m3 | Midpoint Length Right
| AVG | 948000 | 2970 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 65B
2015-04-28 21:19 | 1 | 1310000 | 9680 | /m3 | Midpoint Width Left
| AVG | 1310000 | 9680 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 66B
2015-04-28 21:25 | 1 | 985000 | 6570 | /m3 | Midpoint Width Right
| AVG | 985000 | 6570 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 67B
2015-04-28 21:31 | 1 | 956000 | 7270 | /m3 | Midpoint Length Left
| AVG | 956000 | 7270 | /m3
Point7
Date & time | Times | 0.5um | 5.0um | Unit | Room 21 | File 68B
2015-04-28 23:26 | 1 | 801000 | 3320 | /m3 | Midpoint Length Right
| AVG | 801000 | 3320 | /m3
Point8
Date & time | Times | 0.5um | 5.0um | Unit | Calibration Verification | File 69B
2015-04-28 23:37 | 1 | 212 | 0 | /m3 | Break Room 20
| AVG | 212 | 0 | /m3 | Midpoint Width Left
Point9
Date & time | Times | 0.5um | 5.0um | Unit | Break Room 20 | File 70B
2015-04-28 23:42 | 1 | 1070000 | 2120 | /m3 | Midpoint Width Left
| AVG | 1070000 | 2120 | /m3
Point10
Date & time | Times | 0.5um | 5.0um | Unit | Break Room 20 | File 71B
2015-04-28 23:48 | 1 | 1180000 | 2610 | /m3 | End of Length Back
| AVG | 1180000 | 2610 | /m3
Point11
Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 72B
2015-04-28 23:56 | 1 | 56300 | 2680 | /m3 | Left Side Rear
| AVG | 56300 | 2680 | /m3
Point12
Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 73B
2015-04-29 00:07 | 1 | 3880 | 0 | /m3 | Left Side Front
| AVG | 3880 | 0 | /m3
Point13
Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 74B
2015-04-29 00:17 | 1 | 47600 | 2970 | /m3 | Right Side Rear
| AVG | 47600 | 2970 | /m3
Point14
Date & time | Times | 0.5um | 5.0um | Unit | Room 15 | File 75B
2015-04-29 00:32 | 1 | 12400 | 848 | /m3 | Right Side Front
| AVG | 12400 | 848 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 588000 | 524000 | ---- | /m3
5.0um | 3370 | 2990 | ---- | /m3

## Data 04 30 2015
Point1 |  |  |  |  | Point1
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 76B
2015-04-30 05:13 | 1 | 636 | 0 | /m3 | 2015-04-30 05:13 | 1 | 636 | 0 | /m3 | Zero Filter Test
| AVG | 636 | 0 | /m3 |  | AVG | 636 | 0 | /m3
Point2 |  |  |  |  | Point2
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 77B
2015-04-30 05:19 | 1 | 702000 | 9040 | /m3 | 2015-04-30 05:19 | 1 | 702000 | 9040 | /m3 | Right Side Front
| AVG | 702000 | 9040 | /m3 |  | AVG | 702000 | 9040 | /m3
Point3 |  |  |  |  | Point3
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 78B
2015-04-30 05:25 | 1 | 659000 | 6430 | /m3 | 2015-04-30 05:25 | 1 | 659000 | 6430 | /m3 | Left Side Rear
| AVG | 659000 | 6430 | /m3 |  | AVG | 659000 | 6430 | /m3
Point4 |  |  |  |  | Point4
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 79B
2015-04-30 05:31 | 1 | 682000 | 9180 | /m3 | 2015-04-30 05:31 | 1 | 682000 | 9180 | /m3 | Right Side Middle
| AVG | 682000 | 9180 | /m3 |  | AVG | 682000 | 9180 | /m3
Point5 |  |  |  |  | Point5
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 17 | File 80B
2015-04-30 05:36 | 1 | 869000 | 23800 | /m3 | 2015-04-30 05:36 | 1 | 869000 | 23800 | /m3 | Left Side Middle
| AVG | 869000 | 23800 | /m3 |  | AVG | 869000 | 23800 | /m3
Point6 |  |  |  |  | Point6
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 81B
2015-04-30 05:46 | 1 | 652000 | 3390 | /m3 | 2015-04-30 05:46 | 1 | 652000 | 3390 | /m3 | Left Side Middle
| AVG | 652000 | 3390 | /m3 |  | AVG | 652000 | 3390 | /m3
Point7 |  |  |  |  | Point7
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 82B
2015-04-30 05:56 | 1 | 625000 | 1550 | /m3 | 2015-04-30 05:56 | 1 | 625000 | 1550 | /m3 | Right Side near Ultrasonic Tank
| AVG | 625000 | 1550 | /m3 |  | AVG | 625000 | 1550 | /m3
Point8 |  |  |  |  | Point8
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 83B
2015-04-30 06:03 | 1 | 695000 | 3250 | /m3 | 2015-04-30 06:03 | 1 | 695000 | 3250 | /m3 | Right Side Rear
| AVG | 695000 | 3250 | /m3 |  | AVG | 695000 | 3250 | /m3
Point9 |  |  |  |  | Point9
Date & time | Times | 0.5um | 5.0um | Unit | Date & time | Times | 0.5um | 5.0um | Unit | Room 14 | File 84B
2015-04-30 06:13 | 1 | 716000 | 2750 | /m3 | 2015-04-30 06:13 | 1 | 716000 | 2750 | /m3 | Right Side Front
| AVG | 716000 | 2750 | /m3 |  | AVG | 716000 | 2750 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 622000 | 243000 | 776000 | /m3
5.0um | 6600 | 7200 | 11200 | /m3

## Data 05 05 2015
Handheld LPC Data Retrieval Software
Mode: ISO
Start Time:2000-01-01 12:01:00
Stop Time:2015-05-05 09:54:39
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:01 | 1 | 28300 | 3810 | /m3
| AVG | 28300 | 3810 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:07 | 1 | 69700 | 8970 | /m3
| AVG | 69700 | 8970 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:19 | 1 | 76600 | 7560 | /m3
| AVG | 76600 | 7560 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:25 | 1 | 87200 | 11200 | /m3
| AVG | 87200 | 11200 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:31 | 1 | 77600 | 10100 | /m3
| AVG | 77600 | 10100 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:37 | 1 | 61200 | 8550 | /m3
| AVG | 61200 | 8550 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 66800 | 20800 | 83700 | /m3
5.0um | 8360 | 2550 | 10400 | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:01 | 1 | 13400 | 2260 | /m3
| AVG | 13400 | 2260 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:07 | 1 | 9530 | 1270 | /m3
| AVG | 9530 | 1270 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:13 | 1 | 17700 | 1910 | /m3
| AVG | 17700 | 1910 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:19 | 1 | 15000 | 2540 | /m3
| AVG | 15000 | 2540 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:26 | 1 | 24600 | 4100 | /m3
| AVG | 24600 | 4100 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:31 | 1 | 17900 | 1980 | /m3
| AVG | 17900 | 1980 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 16400 | 5090 | 20500 | /m3
5.0um | 2340 | 958 | 3120 | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:01 | 1 | 9250 | 848 | /m3
| AVG | 9250 | 848 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:07 | 1 | 18300 | 2830 | /m3
| AVG | 18300 | 2830 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:13 | 1 | 11200 | 1980 | /m3
| AVG | 11200 | 1980 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:19 | 1 | 7350 | 1480 | /m3
| AVG | 7350 | 1480 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:25 | 1 | 10500 | 1840 | /m3
| AVG | 10500 | 1840 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:32 | 1 | 13100 | 1620 | /m3
| AVG | 13100 | 1620 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 11600 | 3800 | 14700 | /m3
5.0um | 1770 | 649 | 2300 | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:04 | 1 | 19800000 | 1130 | /m3
| AVG | 19800000 | 1130 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 19800000 | 0 | ---- | /m3
5.0um | 1130 | 0 | ---- | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:23 | 1 | 6140 | 636 | /m3
| AVG | 6140 | 636 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:30 | 1 | 12300 | 1840 | /m3
| AVG | 12300 | 1840 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 12:56 | 1 | 6000 | 1060 | /m3
| AVG | 6000 | 1060 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 01:52 | 1 | 29500 | 4870 | /m3
| AVG | 29500 | 4870 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 02:00 | 1 | 24100 | 3390 | /m3
| AVG | 24100 | 3390 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2000-01-01 02:06 | 1 | 38900 | 6000 | /m3
| AVG | 38900 | 6000 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 19500 | 13500 | 30500 | /m3
5.0um | 2970 | 2160 | 4730 | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 20:42 | 1 | 0 | 0 | /m3
| AVG | 0 | 0 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:07 | 1 | 863000 | 6220 | /m3
| AVG | 863000 | 6220 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:13 | 1 | 948000 | 2970 | /m3
| AVG | 948000 | 2970 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:19 | 1 | 1310000 | 9680 | /m3
| AVG | 1310000 | 9680 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:25 | 1 | 985000 | 6570 | /m3
| AVG | 985000 | 6570 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 21:31 | 1 | 956000 | 7270 | /m3
| AVG | 956000 | 7270 | /m3
Point7
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:26 | 1 | 801000 | 3320 | /m3
| AVG | 801000 | 3320 | /m3
Point8
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:37 | 1 | 212 | 0 | /m3
| AVG | 212 | 0 | /m3
Point9
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:42 | 1 | 1070000 | 2120 | /m3
| AVG | 1070000 | 2120 | /m3
Point10
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:48 | 1 | 1180000 | 2610 | /m3
| AVG | 1180000 | 2610 | /m3
Point11
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-28 23:56 | 1 | 56300 | 2680 | /m3
| AVG | 56300 | 2680 | /m3
Point12
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-29 00:07 | 1 | 3880 | 0 | /m3
| AVG | 3880 | 0 | /m3
Point13
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-29 00:17 | 1 | 47600 | 2970 | /m3
| AVG | 47600 | 2970 | /m3
Point14
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-29 00:32 | 1 | 12400 | 848 | /m3
| AVG | 12400 | 848 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 588000 | 524000 | ---- | /m3
5.0um | 3370 | 2990 | ---- | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 05:13 | 1 | 636 | 0 | /m3
| AVG | 636 | 0 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 05:19 | 1 | 702000 | 9040 | /m3
| AVG | 702000 | 9040 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 05:25 | 1 | 659000 | 6430 | /m3
| AVG | 659000 | 6430 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 05:31 | 1 | 682000 | 9180 | /m3
| AVG | 682000 | 9180 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 05:36 | 1 | 869000 | 23800 | /m3
| AVG | 869000 | 23800 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 05:46 | 1 | 652000 | 3390 | /m3
| AVG | 652000 | 3390 | /m3
Point7
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 05:56 | 1 | 625000 | 1550 | /m3
| AVG | 625000 | 1550 | /m3
Point8
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 06:03 | 1 | 695000 | 3250 | /m3
| AVG | 695000 | 3250 | /m3
Point9
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 06:13 | 1 | 716000 | 2750 | /m3
| AVG | 716000 | 2750 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 622000 | 243000 | 776000 | /m3
5.0um | 6600 | 7200 | 11200 | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 11:13 | 1 | 283 | 0 | /m3
| AVG | 283 | 0 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 11:27 | 1 | 15100 | 565 | /m3
| AVG | 15100 | 565 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 11:35 | 1 | 4240 | 141 | /m3
| AVG | 4240 | 141 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 11:41 | 1 | 12800 | 353 | /m3
| AVG | 12800 | 353 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2015-04-30 11:56 | 1 | 25000 | 1700 | /m3
| AVG | 25000 | 1700 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 11500 | 9680 | 20600 | /m3
5.0um | 551 | 675 | 1180 | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 09:19 | 1 | 70.6 | 0 | /m3
| AVG | 70.6 | 0 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 09:25 | 1 | 16100 | 2050 | /m3
| AVG | 16100 | 2050 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 09:31 | 1 | 10800 | 848 | /m3
| AVG | 10800 | 848 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 09:37 | 1 | 33200 | 2680 | /m3
| AVG | 33200 | 2680 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 09:43 | 1 | 32000 | 2190 | /m3
| AVG | 32000 | 2190 | /m3
Point6
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 09:49 | 1 | 5720 | 283 | /m3
| AVG | 5720 | 283 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 5910 | 5460 | 10400 | /m3
5.0um | 988 | 1150 | 1920 | /m3
Point1
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 09:55 | 1 | 3110 | 212 | /m3
| AVG | 3110 | 212 | /m3
Point2
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 10:02 | 1 | 29900 | 3110 | /m3
| AVG | 29900 | 3110 | /m3
Point3
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 10:08 | 1 | 23000 | 2050 | /m3
| AVG | 23000 | 2050 | /m3
Point4
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 10:14 | 1 | 1620 | 212 | /m3
| AVG | 1620 | 212 | /m3
Point5
Date & time | Times | 0.5um | 5.0um | Unit
2015-05-05 10:19 | 1 | 1200 | 0 | /m3
| AVG | 1200 | 0 | /m3
Pure Class
| AVG | SD | 95%UCL | Unit
0.5um | 5910 | 5460 | 10400 | /m3
5.0um | 988 | 1150 | 1920 | /m3

## ISO vs FED STD 209E Requirement
Class | US FED STD 209E |  |  |  |  | ISO equivalent
Maximum Particles/ft³
| >0.1 um | >0.2 um | >0.3 um | >0.5 um | >5 um
1 | 35 | 7 | 3 | 1 |  | ISO3
10 | 350 | 75 | 30 | 10 |  | ISO4
100 |  |  |  | 100 |  | ISO5
1000 |  |  |  | 1000 | 7 | ISO6
10000 |  |  |  | 10000 | 70 | ISO7
100000 |  |  |  | 100000 | 700 | ISO8
ISO 14644-1 Cleanroom Standards
Class | Maximum Particles/m³ | [5 empty] | FED STD 209E equivalent
| >0.1 um | >0.2 um | >0.3 um | >0.5 um | >1 um | >5 um
ISO 1 | 10 | 2
ISO 2 | 100 | 24 | 10 | 4
ISO 3 | 1000 | 237 | 102 | 35 | 8 |  | Class1
ISO 4 | 10000 | 2370 | 1020 | 352 | 83 |  | Class10
ISO 5 | 100000 | 237000 | 102000 | 35200 | 8320 | 293 | Class 100
ISO 6 | 1000000 | 237000 | 102000 | 35200 | 8320 | 2930 | Class1,000
ISO 7 |  |  |  | 352000 | 83200 | 2930 | Class 10,000
ISO 8 |  |  |  | 3520000 | 832000 | 29300 | Class 100,000
ISO 9 |  |  |  | 35200000 | 8320000 | 293000 | Room Air
Criteria | Class 10 ISO4 | Class 100 ISO5 | Class 1000 ISO6 | Class 10,000 ISO7 | Class 100,000 ISO8
Air changes per HR/Min | 500-600 / 8 to 10 | 300 to 480 / 5 to 8 | 180 / 3 | 60 /1 | 30 / 0.5 |  |  | SO 14644-1 cleanroom standards[edit] |  |  | Reference From: |  |  |  |  | 352000
Filter coverage % | 90 – 100 | 60 – 70 | 20 – 30 | 7 – 15 | 4 – 5 | [5 empty] | http://www.cemag.us/articles/2005/05/iso-class-7-gowning-protocol |  |  |  |  | 2930
CFM per square foot | 85 – 90 | 36 – 65 | 18 – 32 | 9 – 16 | 4 – 8 |  |  | Class | maximum particles/m3 | [5 empty] | FED STD 209E
Filter Efficiency | 99.9997% ULPAs | 99.997% HEPAs | 99.997% HEPAs | 99.997% HEPAs | 99.97% HEPAs |  |  |  | ≥0.1 µm | ≥0.2 µm | ≥0.3 µm | ≥0.5 µm | ≥1 µm | ≥5 µm | equivalent
Ceiling Type | Aluminum T-bar grid | Aluminum T-bar grid | Aluminum T-bar grid | Conventional T-bar grid | Conventional T-bar grid |  |  | ISO 1 | 10 | 2.37 | 1.02 | 0.35 | 0.083 | 0.0029
Light Fixture type | Tear drop or Flow thru | Tear drop or 2’x4’ cleanroom fixture | 2’x4’ cleanroom fixture | 2’x4’ cleanroom fixture | 2’x4’ standard fixture |  |  | ISO 2 | 100 | 23.7 | 10.2 | 3.5 | 0.83 | 0.029
Ceiling Panel | FRP, Vinyl rock or Mylar | FRP, Vinyl rock or Mylar | Vinyl rock or Mylar | Vinyl rock or Mylar | Vinyl rock or Mylar |  |  | ISO 3 | 1000 | 237 | 102 | 35 | 8.3 | 0.29 | Class 1
Wall System | Modular or standard built | Modular or standard built | Modular or standard built | Modular or drywall | Modular or drywall |  |  | ISO 4 | 10000 | 2370 | 1020 | 352 | 83 | 2.9 | Class 10
Flooring cover | Welded sheet vinyl or Epoxy | Welded sheet vinyl or Epoxy | Welded Sheet vinyl or Epoxy | Sheet vinyl or VCT | Sheet vinyl or VCT |  |  | ISO 5 | 100000 | 23700 | 10200 | 3520 | 832 | 29 | Class 100
Flooring base | 2” to 6” cove | Cove or Aluminum base channel | Cove or Aluminum base channel | Cove or Aluminum base channel | Cove or Aluminum base channel |  |  | ISO 6 | 1.0×106 | 237000 | 102000 | 35200 | 8320 | 293 | Class 1,000
Air Returns | Raised floor or center returns | Low wall on long axis | Low wall at perimeter | Low wall | Low wall or ceiling |  |  | ISO 7 | 1.0×107 | 2.37×106 | 1020000 | 352000 | 83200 | 2930 | Class 10,000
[8 empty] | ISO 8 | 1.0×108 | 2.37×107 | 1.02×107 | 3520000 | 832000 | 29300 | Class 100,000
[8 empty] | ISO 9 | 1.0×109 | 2.37×108 | 1.02×108 | 35200000 | 8320000 | 293000 | Room air
Reference taken from: http://www.americancleanrooms.com/cleanroom-classifications/
***Warning***
If we want to certify any of the Cleanrooms to ISO 6 to ISO 3, we will need a new Particle Counter that monitors more than 3 Channels and detects particle sizes down to 0.1 um.

## Sheet7
Reference From:
http://www.cemag.us/articles/2005/05/iso-class-7-gowning-protocol