## Bias Connector
Connector: Glenair GMR7580-21S
Through-Hole
Pins | CCD | Reference | Function | Nominal Voltage | Nominal Current
(mA)
1 | 1 | SS | Substrate | GND
2 | 1 | OG-E | Output Gate (E) | 2V
3 | 1 | OG-F | Output Gate (F) | 2V
4 | 1 | DOD-E, OD-E | Dummy Output Drain (E) Output Drain (E) | 27.5V
5 | 1 | DOD-F, OD-F | Dummy Output Drain (F) Output Drain (F) | 27.5V
6 | 1 | DOD-G, OD-G | Dummy Output Drain (G) Output Drain (G) | 27.5V
7 | 1 | DOD-H, OD-H | Dummy Output Drain (H) Output Drain (H) | 27.5V
8 | 1 | RD-E | Reset Drain (E) | 17V
9 | 1 | DD-A, DD-D | Dump Drain (A), Dump Drain (D) | 26V
10 | 1 | RD-F | Reset Drain (F) | 17V
11 | 1 | OG-G | Output Gate (G) | 2V
12 | 1 | OG-H | Output Gate (H) | 2V
13 | 1 | RD-G | Reset Drain (G) | 17V
14 | 1 | RD-H | Reset Drain (H) | 17V
15 | N/A | Preamp Vcc | Preamp Positive Rail | +5V
16 | N/A | Preamp Vss | Preamp Negative Rail | -5V
17 | N/A | Switch/Receiver Vcc | Digital Logic Positive Rail | +5V
18 | N/A | Switch/Receiver Vcc | Digital Logic Negative Rail | -5V
19 | N/A | Spare
20 | N/A | Spare

## Clock Connector
Connector: Glenair GMR7580-25P
Through-Hole
Pins | CCD | Reference | Function | Nominal High Rail | Nominal Low Rail | Calculated Capacitance | Frequency | Current | Max Current | Min Rise Time
|  |  |  | Volts | Volts | Farad | Hz | mA | mA | us
[9 empty] | 75 ns serial rise 25 us parallel rise | Assume 300 mA Drive Current
1 | 1 | DG-A, DG-D | Dump Gate (A and D) | 12 | 0
2 | 1 | PhiR-E, F, G, H | Reset Gate (E, F, G, H) | 12 | 0
3 | 1 | SW-E, F, G, H | Summing Well (E, F, G, H) | 10 | 1
4 | 1 | E1, H1 | Register Clock Phase 1 (E, H) | 10 | 1 | 6e-10 | 1000000 | 5.4 | 72 | 0.018
5 | 1 | E2, H2 | Register Clock Phase 2(E, H) | 10 | 1 | 5.2e-10 | 1000000 | 4.68 | 62.4 | 0.0156
6 | 1 | E3-F3, G3-H3 | Register Clock Phase 3 (E and F, G and H) | 10 | 1 | 9.2e-10 | 1000000 | 8.28 | 110.4 | 0.0276
7 | 1 | F1, G1 | Register Clock Phase 1 (F, G) | 10 | 1 | 6e-10 | 1000000 | 5.4 | 72 | 0.018
8 | 1 | F2, G2 | Register Clock Phase 2 (F, G) | 10 | 1 | 5.2e-10 | 1000000 | 4.68 | 62.4 | 0.0156
9 | 1 | A4, B4, TG-A | Image Area Clock Phase 4 (A and B), Transfer Gate (A) | 10 | 0 | 1.1017e-07 | 326 | 0.35915 | 44.068 | 3.6723
10 | 1 | A3, B3 | Image Area Clock Phase 3 (A and B) | 10 | 0 | 1.1e-07 | 326 | 0.3586 | 44 | 3.6667
11 | 1 | C4, D4 | Image Area Clock Phase 4 (C and D) | 10 | 0 | 1.1e-07 | 326 | 0.3586 | 44 | 3.6667
12 | 1 | C3, D4 | Image Area Clock Phase 3 (C and D) | 10 | 0 | 1.1e-07 | 326 | 0.3586 | 44 | 3.6667
13 | 1 | C1, D1, TG-D | Image Area Clock Phase 1 (C and D), Transfer Gate (D) | 10 | 0 | 1.1017e-07 | 326 | 0.35915 | 44.068 | 3.6723
14 | 1 | C2, D2 | Image Area Clock Phase 2 (C and D) | 10 | 0 | 1.1e-07 | 326 | 0.3586 | 44 | 3.6667
15 | 1 | A1, B1 | Image Area Clock Phase 1 (A and B) | 10 | 0 | 1.1e-07 | 326 | 0.3586 | 44 | 3.6667
16 | 1 | A2, B2 | Image Area Clock Phase 2 (A and B) | 10 | 0 | 1.1e-07 | 326 | 0.3586 | 44 | 3.6667
17 | N/A | BLC | Black Level Clamp Clock | 5V | 0V
18 | N/A | Spare
19 | N/A | Spare
20 | N/A | Spare
21 | N/A | Spare
22 | N/A | Spare
23 | N/A | Spare
24 | N/A | Spare
25 | N/A | Spare

## Video Connector
Connector: Samtec ERF8-013-05.0-S-DV-L-TR
Surface Mount
Pin | Video | CCD | Reference | Function
1 | N/A | 1 | GND | Twinax Shield
2 | N/A | 1 | GND | Twinax Shield
3 | 1+ | 1 | Signal + (E) | Positive Side Signal (E)
4 | 1- | 1 | Signal - (E) | Negative Side Signal (E)
5 | 2+ | 1 | Signal + (F) | Positive Side Signal (F)
6 | 2- | 1 | Signal - (F) | Negative Side Signal (F)
7 | N/A | 1 | GND | Twinax Shield
8 | N/A | 1 | GND | Twinax Shield
9 | 3+ | 1 | Signal + (G) | Positive Side Signal (G)
10 | 3- | 1 | Signal - (G) | Negative Side Signal (G)
11 | 4+ | 1 | Signal + (H) | Positive Side Signal (H)
12 | 4- | 1 | Signal - (H) | Negative Side Signal (H)
13 | N/A | 1 | GND | Twinax Shield